## WSTECH_Fluence
xid |  | name |  | textRenderer/type | pointLocator/slaveId | pointLocator/range | pointLocator/modbusDataType | pointLocator/offset | pointLocator/multiplier | pointLocator/additive | pointLocator/bit | textRenderer/suffix | pointLocator/writeType | enabled | textRenderer/oneLabel | textRenderer/zeroLabel | textRenderer/format | readPermission | setPermission | tags/deviceFunction | tags/pointMeasure
| APS | 8192 APMC Software Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8192 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8193 APMC Interface Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8193 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8194 APS Active Power Total | 701 WITH SUNSPEC ADDRESS 10 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8194 | 1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8195 APS Active Power L1 | 701 WITH SUNSPEC ADDRESS 41 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8195 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8196 APS Active Power L2 | 701 WITH SUNSPEC ADDRESS 64 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8196 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8197 APS Active Power L3 | 701 WITH SUNSPEC ADDRESS 87 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8197 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8198 APS Reactive Power Total | 701 WITH SUNSPEC ADDRESS 12 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8198 | 1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8199 APS Reactive Power L1 | 701 WITH SUNSPEC ADDRESS 43 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8199 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8200 APS Reactive Power L2 | 701 WITH SUNSPEC ADDRESS 66 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8200 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8201 APS Reactive Power L3 | 701 WITH SUNSPEC ADDRESS 89 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8201 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8202 APS DC Power | 714 WITH SUNSPEC ADDRESS 6 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8202 | 1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8203 Ambient Temperature | 701 WITH SUNSPEC ADDRESS 35 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8203 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8204 Solar Irradiation |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8204 | 0.1 | 0 | 0 | W/m² | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8205 Panel Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8205 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8206 APS Applied Active Power Limit | 704 WITH SUNSPEC ADDRESS 15 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8206 | 1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8210 APS Applied Reactive Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8210 | 1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8214 APS Energy Counter Positive Total | 701 WITH SUNSPEC ADDRESS 19 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8214 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8216 APS Energy Counter Positive L1 | 701 WITH SUNSPEC ADDRESS 48 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8216 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8218 APS Energy Counter Positive L2 | 701 WITH SUNSPEC ADDRESS 71 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8218 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8220 APS Energy Counter Positive L3 | 701 WITH SUNSPEC ADDRESS 94 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8220 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8222 APS Energy Counter Negative Total | 701 WITH SUNSPEC ADDRESS 23 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8222 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8224 APS Energy Counter Negative L1 | 701 WITH SUNSPEC ADDRESS 52 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8224 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8226 APS Energy Counter Negative L2 | 701 WITH SUNSPEC ADDRESS 75 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8226 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8228 APS Energy Counter Negative L3 | 701 WITH SUNSPEC ADDRESS 98 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8228 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8230 APS Error Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8230 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8231 APS Error Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8231 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8232 APS Error Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8232 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8233 APS Error Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8233 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8234 APS Error Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8234 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8235 APS Error Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8235 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8236 APS Error Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8236 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8237 APS Error Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8237 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8254 APS Warning Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8254 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8255 APS Warning Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8255 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8256 APS Warning Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8256 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8257 APS Warning Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8257 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8258 APS Warning Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8258 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8259 APS Warning Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8259 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8260 APS Warning Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8260 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8261 APS Warning Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8261 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8278 APS Operating State |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8278 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8279 APS Modbus TCP Write Error Address |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8279 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 8280 APS MV Trafo Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8280 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8392 APU 1 Grid Voltage L1N | 701 WITH SUNSPEC ADDRESS 47 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8392 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8393 APU 1 Grid Voltage L2N | 701 WITH SUNSPEC ADDRESS 70 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8393 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8394 APU 1 Grid Voltage L3N | 701 WITH SUNSPEC ADDRESS 93 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8394 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8395 APU 1 Grid Voltage L12 | 701 WITH SUNSPEC ADDRESS 46 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8395 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8396 APU 1 Grid Voltage L23 | 701 WITH SUNSPEC ADDRESS 69 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8396 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8397 APU 1 Grid Voltage L31 | 701 WITH SUNSPEC ADDRESS 92 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8397 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8398 APU 1 Grid Frequency | 701 WITH SUNSPEC ADDRESS 17 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8398 | 0.001 | 0 | 0 | Hz | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8399 APU 1 Grid Current L1 | 701 WITH SUNSPEC ADDRESS 45 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8399 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8400 APU 1 Grid Current L2 | 701 WITH SUNSPEC ADDRESS 68 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8400 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8401 APU 1 Grid Current L3 | 701 WITH SUNSPEC ADDRESS 91 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8401 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8402 APU 1 Active Power Total | 701 WITH SUNSPEC ADDRESS 10 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8402 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8403 APU 1 Active Power L1 | 701 WITH SUNSPEC ADDRESS 41 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8403 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8404 APU 1 Active Power L2 | 701 WITH SUNSPEC ADDRESS 64 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8404 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8405 APU 1 Active Power L3 | 701 WITH SUNSPEC ADDRESS 87 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8405 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8406 APU 1 Reactive Power Total | 701 WITH SUNSPEC ADDRESS 12 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8406 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8407 APU 1 Reactive Power L1 | 701 WITH SUNSPEC ADDRESS 43 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8407 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8408 APU 1 Reactive Power L2 | 701 WITH SUNSPEC ADDRESS 66 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8408 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8409 APU 1 Reactive Power L3 | 701 WITH SUNSPEC ADDRESS 89 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8409 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8410 APU 1 DC Voltage | 714 WITH SUNSPEC ADDRESS REP11 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8410 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8411 APU 1 DC Current | 714 WITH SUNSPEC ADDRESS 5 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8411 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8412 APU 1 DC Power | 714 WITH SUNSPEC ADDRESS 6 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8412 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8413 APU 1 Inductor Temperature | 701 WITH SUNSPEC ADDRESS 40 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8413 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8414 APU 1 IGBT Temperature L1 | 701 WITH SUNSPEC ADDRESS 39 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8414 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8415 APU 1 IGBT Temperature L2 | 701 WITH SUNSPEC ADDRESS 39 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8415 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8416 APU 1 IGBT Temperature L3 | 701 WITH SUNSPEC ADDRESS 39 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8416 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8417 APU 1 Applied Active Power Limit | 704 WITH SUNSPEC ADDRESS 15 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8417 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8421 APU 1 Applied Reactive Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8421 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8425 APU 1 Applied DC Voltage Maximum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8425 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8426 APU 1 Applied DC Voltage Minimum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8426 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8427 APU 1 Applied Positive DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8427 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8428 APU 1 Applied Negative DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8428 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8429 APU 1 Energy Counter Positive Total | 701 WITH SUNSPEC ADDRESS 19 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8429 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8431 APU 1 Energy Counter Positive L1 | 701 WITH SUNSPEC ADDRESS 48 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8431 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8433 APU 1 Energy Counter Positive L2 | 701 WITH SUNSPEC ADDRESS 71 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8433 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8435 APU 1 Energy Counter Positive L3 | 701 WITH SUNSPEC ADDRESS 94 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8435 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8437 APU 1 Energy Counter Negative Total | 701 WITH SUNSPEC ADDRESS 23 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8437 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8439 APU 1 Energy Counter Negative L1 | 701 WITH SUNSPEC ADDRESS 52 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8439 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8441 APU 1 Energy Counter Negative L2 | 701 WITH SUNSPEC ADDRESS 75 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8441 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8443 APU 1 Energy Counter Negative L3 | 701 WITH SUNSPEC ADDRESS 98 | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8443 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8445 APU 1 Error Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8445 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8446 APU 1 Error Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8446 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8447 APU 1 Error Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8447 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8448 APU 1 Error Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8448 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8449 APU 1 Error Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8449 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8450 APU 1 Error Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8450 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8451 APU 1 Error Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8451 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8452 APU 1 Error Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8452 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8493 APU 1 Operating State | 701 WITH SUNSPEC ADDRESS 3 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8493 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8494 APU 1 Start Countdown |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8494 | 1 | 0 | 0 | s | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8495 APU 1 Humidity |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8495 | 0.1 | 0 | 0 | %rh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8496 APU 1 PCB Temperature | 701 WITH SUNSPEC ADDRESS 36 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8496 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8497 APU 1 Insulation Resistance | 122 WITH SUNSPEC ADDRESS 44 | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8497 | 0.1 | 0 | 0 | kΩ | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8498 APU 1 Leakage Capacitance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8498 | 0.1 | 0 | 0 | μF | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 8499 APU 1 Firmware Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8499 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8592 APU 2 Grid Voltage L1N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8592 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8593 APU 2 Grid Voltage L2N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8593 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8594 APU 2 Grid Voltage L3N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8594 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8595 APU 2 Grid Voltage L12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8595 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8596 APU 2 Grid Voltage L23 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8596 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8597 APU 2 Grid Voltage L31 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8597 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8598 APU 2 Grid Frequency |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8598 | 0.001 | 0 | 0 | Hz | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8599 APU 2 Grid Current L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8599 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8600 APU 2 Grid Current L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8600 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8601 APU 2 Grid Current L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8601 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8602 APU 2 Active Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8602 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8603 APU 2 Active Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8603 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8604 APU 2 Active Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8604 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8605 APU 2 Active Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8605 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8606 APU 2 Reactive Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8606 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8607 APU 2 Reactive Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8607 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8608 APU 2 Reactive Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8608 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8609 APU 2 Reactive Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8609 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8610 APU 2 DC Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8610 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8611 APU 2 DC Current |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8611 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8612 APU 2 DC Power |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8612 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8613 APU 2 Inductor Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8613 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8614 APU 2 IGBT Temperature L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8614 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8615 APU 2 IGBT Temperature L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8615 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8616 APU 2 IGBT Temperature L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8616 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8617 APU 2 Applied Active Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8617 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8621 APU 2 Applied Reactive Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8621 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8625 APU 2 Applied DC Voltage Maximum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8625 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8626 APU 2 Applied DC Voltage Minimum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8626 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8627 APU 2 Applied Positive DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8627 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8628 APU 2 Applied Negative DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8628 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8629 APU 2 Energy Counter Positive Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8629 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8631 APU 2 Energy Counter Positive L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8631 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8633 APU 2 Energy Counter Positive L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8633 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8635 APU 2 Energy Counter Positive L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8635 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8637 APU 2 Energy Counter Negative Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8437 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8639 APU 2 Energy Counter Negative L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8638 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8641 APU 2 Energy Counter Negative L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8641 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8643 APU 2 Energy Counter Negative L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8643 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8645 APU 2 Error Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8645 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8646 APU 2 Error Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8646 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8647 APU 2 Error Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8647 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8648 APU 2 Error Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8648 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8649 APU 2 Error Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8649 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8650 APU 2 Error Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8650 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8651 APU 2 Error Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8651 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8652 APU 2 Error Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8652 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8693 APU 2 Operating State |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8693 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8694 APU 2 Start Countdown |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8694 | 1 | 0 | 0 | s | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8695 APU 2 Humidity |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8695 | 0.1 | 0 | 0 | %rh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8696 APU 2 PCB Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8696 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8697 APU 2 Insulation Resistance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8697 | 0.1 | 0 | 0 | kΩ | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8698 APU 2 Leakage Capacitance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8698 | 0.1 | 0 | 0 | μF | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 8699 APU 2 Firmware Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8699 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8792 APU 3 Grid Voltage L1N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8792 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8793 APU 3 Grid Voltage L2N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8793 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8794 APU 3 Grid Voltage L3N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8794 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8795 APU 3 Grid Voltage L12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8795 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8796 APU 3 Grid Voltage L23 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8796 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8797 APU 3 Grid Voltage L31 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8797 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8798 APU 3 Grid Frequency |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8798 | 0.001 | 0 | 0 | Hz | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8799 APU 3 Grid Current L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8799 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8800 APU 3 Grid Current L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8800 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8801 APU 3 Grid Current L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8801 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8802 APU 3 Active Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8802 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8803 APU 3 Active Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8803 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8804 APU 3 Active Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8804 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8805 APU 3 Active Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8805 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8806 APU 3 Reactive Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8806 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8807 APU 3 Reactive Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8807 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8808 APU 3 Reactive Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8808 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8809 APU 3 Reactive Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8809 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8810 APU 3 DC Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8810 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8811 APU 3 DC Current |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8811 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8812 APU 3 DC Power |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8812 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8813 APU 3 Inductor Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8813 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8814 APU 3 IGBT Temperature L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8814 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8815 APU 3 IGBT Temperature L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8815 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8816 APU 3 IGBT Temperature L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8816 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8817 APU 3 Applied Active Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8817 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8821 APU 3 Applied Reactive Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8821 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8825 APU 3 Applied DC Voltage Maximum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8825 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8826 APU 3 Applied DC Voltage Minimum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8826 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8827 APU 3 Applied Positive DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8827 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8828 APU 3 Applied Negative DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8828 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8829 APU 3 Energy Counter Positive Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8829 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8831 APU 3 Energy Counter Positive L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8831 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8833 APU 3 Energy Counter Positive L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8833 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8835 APU 3 Energy Counter Positive L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8835 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8837 APU 3 Energy Counter Negative Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8837 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8839 APU 3 Energy Counter Negative L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8838 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8841 APU 3 Energy Counter Negative L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8841 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8843 APU 3 Energy Counter Negative L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 8843 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8845 APU 3 Error Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8845 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8846 APU 3 Error Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8846 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8847 APU 3 Error Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8847 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8848 APU 3 Error Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8848 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8849 APU 3 Error Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8849 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8850 APU 3 Error Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8850 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8851 APU 3 Error Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8851 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8852 APU 3 Error Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8852 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8893 APU 3 Operating State |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8893 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8894 APU 3 Start Countdown |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8894 | 1 | 0 | 0 | s | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8895 APU 3 Humidity |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8895 | 0.1 | 0 | 0 | %rh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8896 APU 3 PCB Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 8896 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8897 APU 3 Insulation Resistance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8897 | 0.1 | 0 | 0 | kΩ | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8898 APU 3 Leakage Capacitance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8898 | 0.1 | 0 | 0 | μF | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 8899 APU 3 Firmware Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8899 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8992 APU 4 Grid Voltage L1N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8992 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8993 APU 4 Grid Voltage L2N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8993 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8994 APU 4 Grid Voltage L3N |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8994 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8995 APU 4 Grid Voltage L12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8995 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8996 APU 4 Grid Voltage L23 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8996 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8997 APU 4 Grid Voltage L31 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8997 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8998 APU 4 Grid Frequency |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8998 | 0.001 | 0 | 0 | Hz | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 8999 APU 4 Grid Current L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 8999 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9000 APU 4 Grid Current L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9000 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9001 APU 4 Grid Current L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9001 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9002 APU 4 Active Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9002 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9003 APU 4 Active Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9003 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9004 APU 4 Active Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9004 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9005 APU 4 Active Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9005 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9006 APU 4 Reactive Power Total |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9006 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9007 APU 4 Reactive Power L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9007 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9008 APU 4 Reactive Power L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9008 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9009 APU 4 Reactive Power L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9009 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9010 APU 4 DC Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9010 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9011 APU 4 DC Current |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9011 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9012 APU 4 DC Power |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9012 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9013 APU 4 Inductor Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9013 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9014 APU 4 IGBT Temperature L1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9014 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9015 APU 4 IGBT Temperature L2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9015 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9016 APU 4 IGBT Temperature L3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9016 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9017 APU 4 Applied Active Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9917 | 0.1 | 0 | 0 | kW | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9021 APU 4 Applied Reactive Power Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9021 | 0.1 | 0 | 0 | kvar | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9025 APU 4 Applied DC Voltage Maximum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9025 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9026 APU 4 Applied DC Voltage Minimum |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9026 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9027 APU 4 Applied Positive DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9027 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9028 APU 4 Applied Negative DC Current Limit |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9028 | 0.1 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9029 APU 4 Energy Counter Positive Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9029 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9031 APU 4 Energy Counter Positive L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9031 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9033 APU 4 Energy Counter Positive L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9033 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9035 APU 4 Energy Counter Positive L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9035 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9037 APU 4 Energy Counter Negative Total |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9037 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9039 APU 4 Energy Counter Negative L1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9038 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9041 APU 4 Energy Counter Negative L2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9041 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9043 APU 4 Energy Counter Negative L3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 9043 | 0.1 | 0 | 0 | kWh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9045 APU 4 Error Code 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9045 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9046 APU 4 Error Code 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9046 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9047 APU 4 Error Code 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9047 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9048 APU 4 Error Code 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9048 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9049 APU 4 Error Code 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9049 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9050 APU 4 Error Code 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9050 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9051 APU 4 Error Code 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9051 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9052 APU 4 Error Code 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9052 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9093 APU 4 Operating State |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9093 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9094 APU 4 Start Countdown |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9094 | 1 | 0 | 0 | s | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9095 APU 4 Humidity |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9095 | 0.1 | 0 | 0 | %rh | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9096 APU 4 PCB Temperature |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 9096 | 0.1 | 0 | 0 | °C | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9097 APU 4 Insulation Resistance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9097 | 0.1 | 0 | 0 | kΩ | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9098 APU 4 Leakage Capacitance |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9098 | 0.1 | 0 | 0 | μF | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 9099 APU 4 Firmware Version |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 9099 | 1 | 0 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10000 APU 1 Positiv Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10000 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10002 APU 1 Negativ Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10002 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10004 APU 1 Current 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10004 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10005 APU 1 PositivAh Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10005 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10007 APU 1 Negativ Ah Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10007 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10009 APU 1 Current 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10009 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10010 APU 1 Positiv Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10010 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10012 APU 1 Negativ Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10012 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10014 APU 1 Current 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10014 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10015 APU 1 Positiv Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10015 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10017 APU 1 Negativ Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10017 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10019 APU 1 Current 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10019 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10020 APU 1 Positiv Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10020 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10022 APU 1 Negativ Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10022 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10024 APU 1 Current 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10024 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10025 APU 1 Positiv Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10025 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10027 APU 1 Negativ Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10027 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10029 APU 1 Current 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10029 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10030 APU 1 Positiv Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10030 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10032 APU 1 Negativ Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10032 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10034 APU 1 Current 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10034 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10035 APU 1 Positiv Ah Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10035 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10037 APU 1 NegativAh Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10037 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10039 APU 1 Current 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10039 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10040 APU 1 Positiv Ah Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10040 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10042 APU 1 NegativAh Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10042 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10044 APU 1 Current 9 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10044 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10045 APU 1 Positiv Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10045 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10047 APU 1 Negativ Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10047 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10049 APU 1 Current 10 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10049 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10050 APU 1 Positiv Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10050 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10052 APU 1 Negativ Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10052 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10054 APU 1 Current 11 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10054 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10055 APU 1 Positiv Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10055 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10057 APU 1 Negativ Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10057 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10059 APU 1 Current 12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10059 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 10060 APU 1 DC Input Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10060 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10100 APU 2 Positiv Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10100 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10102 APU 2 Negativ Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10102 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10104 APU 2 Current 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10104 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10105 APU 2 PositivAh Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10105 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10107 APU 2 Negativ Ah Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10107 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10109 APU 2 Current 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10109 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10110 APU 2 Positiv Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10110 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10112 APU 2 Negativ Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10112 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10114 APU 2 Current 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10114 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10115 APU 2 Positiv Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10115 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10117 APU 2 Negativ Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10117 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10119 APU 2 Current 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10119 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10120 APU 2 Positiv Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10120 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10122 APU 2 Negativ Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10122 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10124 APU 2 Current 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10124 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10125 APU 2 Positiv Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10125 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10127 APU 2 Negativ Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10127 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10129 APU 2 Current 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10129 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10130 APU 2 Positiv Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10130 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10132 APU 2 Negativ Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10132 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10134 APU 2 Current 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10134 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10135 APU 2 Positiv Ah Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10135 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10137 APU 2 NegativAh Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10137 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10139 APU 2 Current 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10139 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10140 APU 2 Positiv Ah Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10140 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10142 APU 2 NegativAh Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10142 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10144 APU 2 Current 9 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10144 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10145 APU 2 Positiv Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10145 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10147 APU 2 Negativ Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10147 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10149 APU 2 Current 10 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10149 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10150 APU 2 Positiv Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10150 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10152 APU 2 Negativ Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10152 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10154 APU 2 Current 11 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10154 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10155 APU 2 Positiv Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10155 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10157 APU 2 Negativ Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10157 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10159 APU 2 Current 12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10159 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 10160 APU 2 DC Input Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10160 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10200 APU 3 Positiv Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10200 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10202 APU 3 Negativ Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10202 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10204 APU 3 Current 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10204 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10205 APU 3 PositivAh Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10205 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10207 APU 3 Negativ Ah Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10207 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10209 APU 3 Current 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10209 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10210 APU 3 Positiv Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10210 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10212 APU 3 Negativ Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10212 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10214 APU 3 Current 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10214 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10215 APU 3 Positiv Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10215 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10217 APU 3 Negativ Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10217 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10219 APU 3 Current 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10219 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10220 APU 3 Positiv Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10220 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10222 APU 3 Negativ Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10222 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10224 APU 3 Current 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10224 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10225 APU 3 Positiv Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10225 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10227 APU 3 Negativ Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10227 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10229 APU 3 Current 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10229 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10230 APU 3 Positiv Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10230 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10232 APU 3 Negativ Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10232 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10234 APU 3 Current 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10234 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10235 APU 3 Positiv Ah Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10235 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10237 APU 3 NegativAh Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10237 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10239 APU 3 Current 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10239 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10240 APU 3 Positiv Ah Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10240 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10242 APU 3 NegativAh Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10242 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10244 APU 3 Current 9 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10244 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10245 APU 3 Positiv Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10245 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10247 APU 3 Negativ Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10247 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10249 APU 3 Current 10 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10249 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10250 APU 3 Positiv Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10250 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10252 APU 3 Negativ Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10252 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10254 APU 3 Current 11 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10254 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10255 APU 3 Positiv Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10255 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10257 APU 3 Negativ Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10257 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10259 APU 3 Current 12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10259 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 10260 APU 3 DC Input Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10260 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10300 APU 4 Positiv Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10300 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10302 APU 4 Negativ Ah Counter 1 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10302 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10304 APU 4 Current 1 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10304 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10305 APU 4 PositivAh Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10305 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10307 APU 4 Negativ Ah Counter 2 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10307 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10309 APU 4 Current 2 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10309 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10310 APU 4 Positiv Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10310 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10312 APU 4 Negativ Ah Counter 3 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10312 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10314 APU 4 Current 3 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10314 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10315 APU 4 Positiv Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10315 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10317 APU 4 Negativ Ah Counter 4 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10317 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10319 APU 4 Current 4 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10319 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10320 APU 4 Positiv Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10320 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10322 APU 4 Negativ Ah Counter 5 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10322 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10324 APU 4 Current 5 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10324 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10325 APU 4 Positiv Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10325 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10327 APU 4 Negativ Ah Counter 6 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10327 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10329 APU 4 Current 6 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10329 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10330 APU 4 Positiv Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10330 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10332 APU 4 Negativ Ah Counter 7 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10332 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10334 APU 4 Current 7 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10334 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10335 APU 4 Positiv Ah Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10335 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10337 APU 4 NegativAh Counter 8 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10337 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10339 APU 4 Current 8 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10339 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10340 APU 4 Positiv Ah Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10340 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10342 APU 4 NegativAh Counter 9 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10342 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10344 APU 4 Current 9 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 1044 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10345 APU 4 Positiv Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10345 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10347 APU 4 Negativ Ah Counter 10 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10347 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10349 APU 4 Current 10 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10349 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10350 APU 4 Positiv Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10350 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10352 APU 4 Negativ Ah Counter 11 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10352 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10354 APU 4 Current 11 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10354 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10355 APU 4 Positiv Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10355 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10357 APU 4 Negativ Ah Counter 12 |  | ANALOG | 1 | INPUT_REGISTER | FOUR_BYTE_INT_UNSIGNED | 10357 | 0.01 | 0 | 0 | Ah | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10359 APU 4 Current 12 |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10359 | 0.01 | 0 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 10360 APU 4 DC Input Voltage |  | ANALOG | 1 | INPUT_REGISTER | TWO_BYTE_INT_UNSIGNED | 10360 | 0.1 | 0 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 24576 APS Active Power Set Point | 704 WITH SUNSPEC ADDRESS 24 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24576 | 1 | 0 | 0 | kW | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 24580 APS Reactive Power Set Point | 704 WITH SUNSPEC ADDRESS 38 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24580 | 1 | 0 | 0 | kvar | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APS | 24584 APS Island Voltage Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24584 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0130± 10%
| APS | 24585 APS Island Frequency Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24585 | 0.001 | 0 | 0 | Hz | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0120± 5Hz.
| APS | 24586 APS Operating Mode |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24586 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...4000
| APS | 24587 APS Error Reset |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24587 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APS | 24588 APS Activate Modbus TCP Interface |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24588 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APS | 24589 APS Heartbeat | 715 WITH SUNSPEC ADDRESS 3 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24589 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...65535
| APU 1 | 24596 APU 1 Active Power Set Point | 704 WITH SUNSPEC ADDRESS 24 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24596 | 0.1 | 0 | 0 | kW | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24600 APU 1 Reactive Power Set Point | 704 WITH SUNSPEC ADDRESS 38 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24600 | 0.1 | 0 | 0 | kvar | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24604 APU 1 DC Voltage Maximum | 121 WITH SUNSPEC ADDRESS 5 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24604 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24605 APU 1 DC Voltage Minimum | 121 WITH SUNSPEC ADDRESS 6 | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24605 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24606 APU 1 Positive DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24606 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24607 APU 1 Negative DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24607 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 1 | 24608 APU 1 Island Voltage Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24608 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0130± 10%
| APU 1 | 24609 APU 1 Island Frequency Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24609 | 0.001 | 0 | 0 | Hz | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0120± 5Hz.
| APU 1 | 24610 APU 1 Operating Mode |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24610 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...4000
| APU 1 | 24611 APU 1 Error Reset |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24611 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APU 1 | 24612 APU 1 Heartbeat |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24612 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...65535
| APU 2 | 24626 APU 2 Active Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24626 | 0.1 | 0 | 0 | kW | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24630 APU 2 Reactive Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24630 | 0.1 | 0 | 0 | kvar | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24634 APU 2 DC Voltage Maximum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24634 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24635 APU 2 DC Voltage Minimum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24635 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24636 APU 2 Positive DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24636 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24637 APU 2 Negative DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24637 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 2 | 24638 APU 2 Island Voltage Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24638 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0130± 10%
| APU 2 | 24639 APU 2 Island Frequency Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24639 | 0.001 | 0 | 0 | Hz | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0120± 5Hz.
| APU 2 | 24640 APU 2 Operating Mode |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24640 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...4000
| APU 2 | 24641 APU 2 Error Reset |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24641 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APU 2 | 24642 APU 2 Heartbeat |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24642 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...65535
| APU 3 | 24656 APU 3 Active Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24656 | 0.1 | 0 | 0 | kW | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24660 APU 3 Reactive Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24660 | 0.1 | 0 | 0 | kvar | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24664 APU 3 DC Voltage Maximum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24664 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24665 APU 3 DC Voltage Minimum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24665 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24666 APU 3 Positive DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24666 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24667 APU 3 Negative DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24667 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 3 | 24668 APU 3 Island Voltage Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24668 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0130± 10%
| APU 3 | 24669 APU 3 Island Frequency Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24669 | 0.001 | 0 | 0 | Hz | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0120± 5Hz.
| APU 3 | 24670 APU 3 Operating Mode |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24670 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...4000
| APU 3 | 24671 APU 3 Error Reset |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24671 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APU 3 | 24672 APU 3 Heartbeat |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24672 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...65535
| APU 4 | 24686 APU 4 Active Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24686 | 0.1 | 0 | 0 | kW | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24690 APU 4 Reactive Power Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24690 | 0.1 | 0 | 0 | kvar | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24694 APU 4 DC Voltage Maximum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24694 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24695 APU 4 DC Voltage Minimum |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24695 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24696 APU 4 Positive DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24696 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24697 APU 4 Negative DC Current Limit |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24697 | 0.1 | 0 | 0 | A | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter
| APU 4 | 24698 APU 4 Island Voltage Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24698 | 0.1 | 0 | 0 | V | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0130± 10%
| APU 4 | 24699 APU 4 Island Frequency Set Point |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24699 | 0.001 | 0 | 0 | Hz | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | DS0120± 5Hz.
| APU 4 | 24700 APU 4 Operating Mode |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24700 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...4000
| APU 4 | 24701 APU 4 Error Reset |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24701 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...1
| APU 4 | 24702 APU 4 Heartbeat |  | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_UNSIGNED | 24702 | 1 | 0 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | read-only,full-access,inverter, wstech | full-access,inverter,wstech | inverter | 0...65535

## WSTECH_APS_Device_Templet
ResourceSet | ParentResourceSet | Source | Sunspec Model Index | Repeat Block Marker | Sunspec Resource Tag | SunSpec bitindex | SunSpec bitfield name | Vendor bitindex | FluenceCanonicalResourceName | Current Fluence Name | Manufacturer Resource Name | SunspecMandatory | SunSpec Label | Description | Vendor data type | Conversion Adder | SunSpec Data Type | Vendor Units | Conversion Multiplier | SunSpec Units | Register Size(Vendor) | Register Size(SunSpec) | Sunspec Register Address | Vendor Register Address | VendorPrimaryTable | SunspecScaleFactor | FluenceDefaultEnabled | Default Polling Frequency | Access | Remark
APS | Wstech | SunSpec | 701 |  | ACType | [7 empty] | AC Wiring Type | AC wiring type. |  |  | enum16 |  |  |  |  | 1 | 2
APS | Wstech | SunSpec | 701 |  | St | [7 empty] | Operating State | Operating state of the DER. |  |  | enum16 |  |  |  |  | 1 | 3
APS | Wstech | SunSpec | 701 |  | InvSt | [7 empty] | Inverter State | Enumerated value. Inverter state. |  |  | enum16 |  |  |  |  | 1 | 4
APS | Wstech | SunSpec | 701 |  | ConnSt | [7 empty] | Grid Connection State | Grid connection state of the DER. |  |  | enum16 |  |  |  |  | 1 | 5
APS | Wstech | SunSpec | 701 |  | Alrm | [7 empty] | Alarm Bitfield | Active alarms for the DER. |  |  | bitfield32 |  |  |  |  | 2 | 6
APS | Wstech | SunSpec | 701 |  | Alrm | 0 | GROUND_FAULT | [5 empty] | Ground Fault
APS | Wstech | SunSpec | 701 |  | Alrm | 1 | DC_OVER_VOLT | [5 empty] | DC Over Voltage
APS | Wstech | SunSpec | 701 |  | Alrm | 2 | AC_DISCONNECT | [5 empty] | AC Disconnect Open
APS | Wstech | SunSpec | 701 |  | Alrm | 3 | DC_DISCONNECT | [5 empty] | DC Disconnect Open
APS | Wstech | SunSpec | 701 |  | Alrm | 4 | GRID_DISCONNECT | [5 empty] | Grid Disconnect
APS | Wstech | SunSpec | 701 |  | Alrm | 5 | CABINET_OPEN | [5 empty] | Cabinet Open
APS | Wstech | SunSpec | 701 |  | Alrm | 6 | MANUAL_SHUTDOWN | [5 empty] | Manual Shutdown
APS | Wstech | SunSpec | 701 |  | Alrm | 7 | OVER_TEMP | [5 empty] | Over Temperature
APS | Wstech | SunSpec | 701 |  | Alrm | 8 | OVER_FREQUENCY | [5 empty] | Frequency Above Limit
APS | Wstech | SunSpec | 701 |  | Alrm | 9 | UNDER_FREQUENCY | [5 empty] | Frequency Under Limit
APS | Wstech | SunSpec | 701 |  | Alrm | 10 | AC_OVER_VOLT | [5 empty] | AC Voltage Above Limit
APS | Wstech | SunSpec | 701 |  | Alrm | 11 | AC_UNDER_VOLT | [5 empty] | AC Voltage Under Limit
APS | Wstech | SunSpec | 701 |  | Alrm | 12 | BLOWN_STRING_FUSE | [5 empty] | Blown String Fuse On Input
APS | Wstech | SunSpec | 701 |  | Alrm | 13 | UNDER_TEMP | [5 empty] | Under Temperature
APS | Wstech | SunSpec | 701 |  | Alrm | 14 | MEMORY_LOSS | [5 empty] | Generic Memory Or Communication Error (Internal)
APS | Wstech | SunSpec | 701 |  | Alrm | 15 | HW_TEST_FAILURE | [5 empty] | Hardware Test Failure
APS | Wstech | SunSpec | 701 |  | Alrm | 16 | MANUFACTURER_ALRM | [5 empty] | Manufacturer Alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
APS | Wstech | SunSpec | 701 |  | DERMode | [7 empty] | DER Operational Characteristics | Current operational characteristics of the DER. |  |  | bitfield32 |  |  |  |  | 2 | 8
APS | Wstech | SunSpec | 701 |  | DERMode | 0 | GRID_FOLLOWING | [5 empty] | Grid Following | The DER is operating as part of a larger grid.
APS | Wstech | SunSpec | 701 |  | DERMode | 1 | GRID_FORMING | [5 empty] | Grid Forming | The DER is providing the grid.
APS | Wstech | SunSpec | 701 |  | DERMode | 2 | PV_CLIPPED | [5 empty] | PV Output Clipped | The PV output is clipped.
APS | Wstech | SunSpec | 701 |  | W |  |  |  | W | APS Active Power Total | APS Active Power Total |  | Active Power | Total active power. | INT16 |  | int16 | KW/1 | 1000 | W | 1 | 1 | 10 | 8194 | INPUT_REGISTER | W_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | VA | [7 empty] | Apparent Power | Total apparent power. |  |  | int16 |  |  | VA |  | 1 | 11
APS | Wstech | SunSpec | 701 |  | Var |  |  |  | VA | APS Reactive Power Total | APS Reactive Power Total |  | Reactive Power | Total reactive power. | INT16 |  | int16 | KVAR/1 | 1000 | Var | 1 | 1 | 12 | 8198 | INPUT_REGISTER | Var_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | PF | [7 empty] | Power Factor | Power factor. |  |  | uint16 |  |  |  |  | 1 | 13
APS | Wstech | SunSpec | 701 |  | A | [7 empty] | Total AC Current | Total AC current. |  |  | int16 |  |  | A |  | 1 | 14
APS | Wstech | SunSpec | 701 |  | LLV | [7 empty] | Voltage LL | Line to line AC voltage as an average of active phases. |  |  | uint16 |  |  | V |  | 1 | 15
APS | Wstech | SunSpec | 701 |  | LNV | [7 empty] | Voltage LN | Line to neutral AC voltage as an average of active phases. |  |  | uint16 |  |  | V |  | 1 | 16
APS | Wstech | SunSpec | 701 |  | Hz | [7 empty] | Frequency | AC frequency. |  |  | uint32 |  |  | Hz |  | 2 | 17
APS | Wstech | SunSpec | 701 |  | TotWhInj |  |  |  | TotWhInj | APS Energy Counter Positive Total | APS Energy Counter Positive Total |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4). | UINT32 |  | ` | KWH/10 | 1000 | Wh | 2 | 4 | 19 | 8214 | INPUT_REGISTER | TotWh_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotWhAbs |  |  |  | TotWhAbs | APS Energy Counter Negative Total | APS Energy Counter Negative Total |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3). | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 23 | 8222 | INPUT_REGISTER | TotWh_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotVarhInj | [7 empty] | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2). |  |  | uint64 |  |  | Varh |  | 4 | 27
APS | Wstech | SunSpec | 701 |  | TotVarhAbs | [7 empty] | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4). |  |  | uint64 |  |  | Varh |  | 4 | 31
APS | Wstech | SunSpec | 701 |  | TmpAmb |  |  |  | TmpAmb |  | Ambient Temperature |  | Ambient Temperature | Ambient temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 35 | 8203 | INPUT_REGISTER | Tmp_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TmpCab |  |  |  | TmpCab |  | Panel Temperature |  | Cabinet Temperature | Cabinet Temperature | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 36 | 8205 | INPUT_REGISTER | Tmp_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TmpSnk | [7 empty] | Heat Sink Temperature | Heat sink temperature. |  |  | int16 |  |  | C |  | 1 | 37
APS | Wstech | SunSpec | 701 |  | TmpTrns | [7 empty] | Transformer Temperature | Transformer temperature. |  |  | int16 |  |  | C |  | 1 | 38
APS | Wstech | SunSpec | 701 |  | TmpSw | [7 empty] | IGBT/MOSFET Temperature | IGBT/MOSFET temperature. |  |  | int16 |  |  | C |  | 1 | 39
APS | Wstech | SunSpec | 701 |  | TmpOt | [7 empty] | Other Temperature | Other temperature. |  |  | int16 |  |  | C |  | 1 | 40
APS | Wstech | SunSpec | 701 |  | WL1 |  |  |  | WL1 | APS Active Power L1 | APS Active Power L1 |  | Watts L1 | Active power L1. | INT16 |  | int16 | KW/10 | 1000 | W | 1 | 1 | 41 | 8195 | INPUT_REGISTER | W_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | VAL1 | [7 empty] | VA L1 | Apparent power L1. |  |  | int16 |  |  | VA |  | 1 | 42
APS | Wstech | SunSpec | 701 |  | VarL1 |  |  |  | VarL1 | APS Reactive Power L1 | APS Reactive Power L1 |  | Var L1 | Reactive power L1. | INT16 |  | int16 | KVAR/10 | 1000 | Var | 1 | 1 | 43 | 8199 | INPUT_REGISTER | Var_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | PFL1 | [7 empty] | PF L1 | Power factor phase L1. |  |  | uint16 |  |  |  |  | 1 | 44
APS | Wstech | SunSpec | 701 |  | AL1 | [7 empty] | Amps L1 | Current phase L1. |  |  | int16 |  |  | A |  | 1 | 45
APS | Wstech | SunSpec | 701 |  | VL1L2 | [7 empty] | Phase Voltage L1-L2 | Phase voltage L1-L2. |  |  | uint16 |  |  | V |  | 1 | 46
APS | Wstech | SunSpec | 701 |  | VL1 | [7 empty] | Phase Voltage L1-N | Phase voltage L1-N. |  |  | uint16 |  |  | V |  | 1 | 47
APS | Wstech | SunSpec | 701 |  | TotWhInjL1 |  |  |  | TotWhInjL1 | APS Energy Counter Positive L1 | APS Energy Counter Positive L1 |  | Total Watt-Hours Inj L1 | Total active energy injected L1. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 48 | 8216 | INPUT_REGISTER | TotWh_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotWhAbsL1 |  |  |  | TotWhAbsL1 |  |  |  | Total Watt-Hours Abs L1 | Total active energy absorbed L1. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 52 | 8224 | INPUT_REGISTER | TotWh_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotVarhInjL1 | [7 empty] | Total Var-Hours Inj L1 | Total reactive energy injected L1. |  |  | uint64 |  |  | Varh |  | 4 | 56
APS | Wstech | SunSpec | 701 |  | TotVarhAbsL1 | [7 empty] | Total Var-Hours Abs L1 | Total reactive energy absorbed L1. |  |  | uint64 |  |  | Varh |  | 4 | 60
APS | Wstech | SunSpec | 701 |  | WL2 |  |  |  | WL2 | APS Active Power L2 | APS Active Power L2 |  | Watts L2 | Active power L2. | INT16 |  | int16 | KW/10 | 1000 | W | 1 | 1 | 64 | 8196 | INPUT_REGISTER | W_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | VAL2 | [7 empty] | VA L2 | Apparent power L2. |  |  | int16 |  |  | VA |  | 1 | 65
APS | Wstech | SunSpec | 701 |  | VarL2 |  |  |  | VarL2 | APS Reactive Power L2 | APS Reactive Power L2 |  | Var L2 | Reactive power L2. | INT16 |  | int16 | KVAR/10 | 1000 | Var | 1 | 1 | 66 | 8200 | INPUT_REGISTER | Var_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | PFL2 | [7 empty] | PF L2 | Power factor L2. |  |  | uint16 |  |  |  |  | 1 | 67
APS | Wstech | SunSpec | 701 |  | AL2 | [7 empty] | Amps L2 | Current L2. |  |  | int16 |  |  | A |  | 1 | 68
APS | Wstech | SunSpec | 701 |  | VL2L3 | [7 empty] | Phase Voltage L2-L3 | Phase voltage L2-L3. |  |  | uint16 |  |  | V |  | 1 | 69
APS | Wstech | SunSpec | 701 |  | VL2 | [7 empty] | Phase Voltage L2-N | Phase voltage L2-N. |  |  | uint16 |  |  | V |  | 1 | 70
APS | Wstech | SunSpec | 701 |  | TotWhInjL2 |  |  |  | TotWhInjL2 | APS Energy Counter Positive L2 | APS Energy Counter Positive L2 |  | Total Watt-Hours Inj L2 | Total active energy injected L2. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 71 | 8218 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotWhAbsL2 |  |  |  | TotWhAbsL2 | APS Energy Counter Negative L2 | APS Energy Counter Negative L2 |  | Total Watt-Hours Abs L2 | Total active energy absorbed L2. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 75 | 8226 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotVarhInjL2 | [7 empty] | Total Var-Hours Inj L2 | Total reactive energy injected L2. |  |  | uint64 |  |  | Varh |  | 4 | 79
APS | Wstech | SunSpec | 701 |  | TotVarhAbsL2 | [7 empty] | Total Var-Hours Abs L2 | Total reactive energy absorbed L2. |  |  | uint64 |  |  | Varh |  | 4 | 83
APS | Wstech | SunSpec | 701 |  | WL3 |  |  |  | WL3 | APS Active Power L3 | APS Active Power L3 |  | Watts L3 | Active power L3. | INT16 |  | int16 | KW/10 | 1000 | W | 1 | 1 | 87 | 8197 | INPUT_REGISTER | W_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | VAL3 | [7 empty] | VA L3 | Apparent power L3. |  |  | int16 |  |  | VA |  | 1 | 88
APS | Wstech | SunSpec | 701 |  | VarL3 |  |  |  | VarL3 | APS Reactive Power L3 | APS Reactive Power L3 |  | Var L3 | Reactive power L3. | INT16 |  | int16 | KVAR/10 | 1000 | Var | 1 | 1 | 89 | 8201 | INPUT_REGISTER | Var_SF |  |  | RO
APS | Wstech | SunSpec | 701 |  | PFL3 | [7 empty] | PF L3 | Power factor L3. |  |  | uint16 |  |  |  |  | 1 | 90
APS | Wstech | SunSpec | 701 |  | AL3 | [7 empty] | Amps L3 | Current L3. |  |  | int16 |  |  | A |  | 1 | 91
APS | Wstech | SunSpec | 701 |  | VL3L1 | [7 empty] | Phase Voltage L3-L1 | Phase voltage L3-L1. |  |  | uint16 |  |  | V |  | 1 | 92
APS | Wstech | SunSpec | 701 |  | VL3 | [7 empty] | Phase Voltage L3-N | Phase voltage L3-N. |  |  | uint16 |  |  | V |  | 1 | 93
APS | Wstech | SunSpec | 701 |  | TotWhInjL3 |  |  |  | TotWhInjL3 | APS Energy Counter Positive L3 | APS Energy Counter Positive L3 |  | Total Watt-Hours Inj L3 | Total active energy injected L3. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 94 | 8220 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotWhAbsL3 |  |  |  | TotWhAbsL3 | APS Energy Counter Negative L3 | APS Energy Counter Negative L3 |  | Total Watt-Hours Abs L3 | Total active energy absorbed L3. | UINT32 |  | uint64 | KWH/10 | 1000 | Wh | 2 | 4 | 98 | 8228 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | SunSpec | 701 |  | TotVarhInjL3 | [7 empty] | Total Var-Hours Inj L3 | Total reactive energy injected L3. |  |  | uint64 |  |  | Varh |  | 6 | 102
APS | Wstech | SunSpec | 701 |  | TotVarhAbsL3 | [7 empty] | Total Var-Hours Abs L3 | Total reactive energy absorbed L3. |  |  | uint64 |  |  | Varh |  | 6 | 106
APS | Wstech | SunSpec | 701 |  | ThrotPct | [7 empty] | Throttling In Pct | Throttling in pct of maximum active power. |  |  | uint16 |  |  | Pct |  | 1 | 110
APS | Wstech | SunSpec | 701 |  | ThrotSrc | [7 empty] | Throttle Source Information | Active throttling source. |  |  | bitfield32 |  |  |  |  | 2 | 111
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 0 | MAX_W
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 1 | FIXED_W
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 2 | FIXED_VAR
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 3 | FIXED_PF
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 4 | VOLT_VAR
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 5 | FREQ_WATT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 6 | DYN_REACT_CURR
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 7 | LVRT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 8 | HVRT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 9 | WATT_VAR
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 10 | VOLT_WATT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 11 | SCHEDULED
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 12 | LFRT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 13 | HFRT
APS | Wstech | SunSpec | 701 |  | ThrotSrc | 14 | DERATED
APS | Wstech | SunSpec | 701 |  | A_SF | [7 empty] | Current Scale Factor | Current scale factor. |  |  | sunssf | [5 empty] | 113
APS | Wstech | SunSpec | 701 |  | V_SF | [7 empty] | Voltage Scale Factor | Voltage scale factor. |  |  | sunssf | [5 empty] | 114
APS | Wstech | SunSpec | 701 |  | Hz_SF | [7 empty] | Frequency Scale Factor | Frequency scale factor. |  |  | sunssf | [5 empty] | 115
APS | Wstech | SunSpec | 701 |  | W_SF | [7 empty] | Active Power Scale Factor | Active power scale factor. |  |  | sunssf | [5 empty] | 116
APS | Wstech | SunSpec | 701 |  | PF_SF | [7 empty] | Power Factor Scale Factor | Power factor scale factor. |  |  | sunssf | [5 empty] | 117
APS | Wstech | SunSpec | 701 |  | VA_SF | [7 empty] | Apparent Power Scale Factor | Apparent power scale factor. |  |  | sunssf | [5 empty] | 118
APS | Wstech | SunSpec | 701 |  | Var_SF | [7 empty] | Reactive Power Scale Factor | Reactive power scale factor. |  |  | sunssf | [5 empty] | 119
APS | Wstech | SunSpec | 701 |  | TotWh_SF | [7 empty] | Active Energy Scale Factor | Active energy scale factor. |  |  | sunssf | [5 empty] | 120
APS | Wstech | SunSpec | 701 |  | TotVarh_SF | [7 empty] | Reactive Energy Scale Factor | Reactive energy scale factor. |  |  | sunssf | [5 empty] | 121
APS | Wstech | SunSpec | 701 |  | Tmp_SF | [7 empty] | Temperature Scale Factor | Temperature scale factor. |  |  | sunssf | [5 empty] | 122
APS | Wstech | SunSpec | 701 |  | MnAlrmInfo | [7 empty] | Manufacturer Alarm Info | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. |  |  | string | [5 empty] | 123
APS | Wstech | SunSpec | 714 |  | DCW |  |  |  | DCW | APS DC Power | APS DC Power |  | DC Power | Total DC power for all ports. | INT16 |  | INT16 | KW/10 | 1000 | W | 1 | 1 | 6 | 8202 | INPUT_REGISTER | DCW_SF |  |  | RO
APS | Wstech | SunSpec | 704 |  | WSet |  |  |  | WSet | APS Active Power Set Point | APS Active Power Set Point |  | Active Power Setpoint (W) | Active power setting value in watts. | INT16 |  | INT32 | KW/10 | 1000 | W | 1 | 2 | 24 | 24576 | HOLDING_REGISTER | WSet_SF |  |  | RW
APS | Wstech | SunSpec | 704 |  | VarSet |  |  |  | VarSet | APS Reactive Power Set Point | APS Reactive Power Set Point |  |  | APS Reactive Power Set Point | INT16 |  | INT32 | Kvar/10 | 1000 | Var | 1 | 2 | 38 | 24580 | HOLDING_REGISTER | VarSet_SF |  |  | RW
APU | Wstech | SunSpec | 715 |  | DERHb |  |  |  | DERHb | APS Heartbeat | APS Heartbeat |  | DER Heartbeat | Value is incremented every second by the DER with periodic resets to zero. | UINT16 |  | UNIT32 |  | 1 |  | 1 | 2 | 3 | 24589 | HOLDING_REGISTER |  |  |  | RO |  | RO
APU | Wstech | Vendor | 64092 | [5 empty] | APSIslandVoltSetPoint | APS Island Voltage Set Point | APS Island Voltage Set Point |  |  | APS Island Voltage Set Point | UINT16 |  |  | V/10 | 1 |  | 1 |  |  | 24584 | HOLDING_REGISTER |  |  |  | RO
APU | Wstech | Vendor | 64092 | [5 empty] | APSIslandFrSetPoint | APS Island Frequency Set Point | APS Island Frequency Set Point |  |  | APS Island Frequency Set Point | UINT16 |  |  | Hz/1000 | 1 |  | 1 |  |  | 24585 | HOLDING_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSAppVArPowLim | APS Applied Reactive Power Limit | APS Applied Reactive Power Limit |  |  | APS Applied Reactive Power Limit | INT16 |  |  | KVar | 1 |  | 1 |  |  | 8210 | INPUT_REGISTER |  |  |  | RO
APU | Wstech | Vendor | 64092 | [5 empty] | APU1ErrorRst | APU 1 Error Reset | APU 1 Error Reset |  |  | APU 1 Error Reset | UINT16 |  |  |  | 1 |  | 1 |  |  | 24587 | HOLDING_REGISTER |  |  |  | RO
APU | Wstech | Vendor | 64092 | [5 empty] | APSActModbusTCPInt | APS Activate Modbus TCP Interface | APS Activate Modbus TCP Interface |  |  | APS Activate Modbus TCP Interface | UINT16 |  |  |  | 1 |  | 1 |  |  | 24588 | HOLDING_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APMCSoftVersion | APMC Software Version | APMC Software Version |  |  | APMC Software Version | UINT16 |  | - | - | 1 |  | 1 |  |  | 8192 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APMCIntrfaceVersion | APMC Interface Version | APMC Interface Version |  |  | APMC Interface Version | UINT16 |  |  |  | 1 |  | 1 |  |  | 8193 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | SolarIrrad | Solar Irradiation | Solar Irradiation |  |  | Solar Irradiation | UINT16 |  |  | W/M2/10 | 1 |  | 1 |  |  | 8204 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSModTCPWriteErrorAddress | APS Modbus TCP Write Error Address | APS Modbus TCP Write Error Address |  |  | APS Modbus TCP Write Error Address | UINT16 |  |  |  | 1 |  | 1 |  |  | 8279 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSMVTrafoTemp | APS MV Trafo Temperature | APS MV Trafo Temperature |  |  | APS MV Trafo Temperature | INT16 |  |  | C/10 | 1 |  | 1 |  |  | 8280 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes1 | APS Error Code 1 | APS Error Code 1 |  |  | APS Error Code 1 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8230 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode1 | APS Warning Code 1 | APS Warning Code 1 |  |  | APS Warning Code 1 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8254 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSOpModes | APS Operating Modes | APS Operating Modes |  |  | APS Operating Modes | UINT16 |  |  |  | 1 |  | 1 |  |  | 24586 | HOLDING_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSOpSt | APS Operating States | APS Operating States |  |  | APS Operating States | UINT16 |  |  |  | 1 |  | 1 |  |  | 8278 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes2 | APS Error Code 2 | APS Error Code 2 |  |  | APS Error Code 2 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8231 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode2 | APS Warning Code 2 | APS Warning Code 2 |  |  | APS Warning Code 2 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8255 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes3 | APS Error Code 3 | APS Error Code 3 |  |  | APS Error Code 3 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8232 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode3 | APS Warning Code 3 | APS Warning Code 3 |  |  | APS Warning Code 3 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8256 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes4 | APS Error Code 4 | APS Error Code 4 |  |  | APS Error Code 4 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8233 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode4 | APS Warning Code 4 | APS Warning Code 4 |  |  | APS Warning Code 4 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8257 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes5 | APS Error Code 5 | APS Error Code 5 |  |  | APS Error Code 5 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8234 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode5 | APS Warning Code 5 | APS Warning Code 5 |  |  | APS Warning Code 5 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8258 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes6 | APS Error Code 6 | APS Error Code 6 |  |  | APS Error Code 6 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8235 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode6 | APS Warning Code 6 | APS Warning Code 6 |  |  | APS Warning Code 6 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8259 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes7 | APS Error Code 7 | APS Error Code 7 |  |  | APS Error Code 7 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8236 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode7 | APS Warning Code 7 | APS Warning Code 7 |  |  | APS Warning Code 7 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8260 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | ApsErrorCodes8 | APS Error Code 8 | APS Error Code 8 |  |  | APS Error Code 8 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8237 | INPUT_REGISTER |  |  |  | RO
APS | Wstech | Vendor | 64092 | [5 empty] | APSWarnCode8 | APS Warning Code 8 | APS Warning Code 8 |  |  | APS Warning Code 8 | UINT16 |  |  |  | 1 |  | 1 |  |  | 8261 | INPUT_REGISTER |  |  |  | RO

## WSTECH_APU_Device_Templet
ResourceSet | ParentResourceSet | Source | Sunspec Model Index | Repeat Block Marker | Sunspec Resource Tag | SunSpec bitindex | SunSpec bitfield name | Vendor bitindex | FluenceCanonicalResourceName | Current Fluence Name | Manufacturer Resource Name | SunspecMandatory | SunSpec Label | Description | Vendor data type | Conversion Adder | SunSpec Data Type | Vendor Units | Conversion Multiplier | SunSpec Units | Register Size(Vendor) | Register Size(SunSpec) | Sunspec Register Address | Vendor Register Address | Address Offset | VendorPrimaryTable | SunspecScaleFactor | FluenceDefaultEnabled | Default Polling Frequency | Access | Remark
APU 1 | APS | SunSpec | 701 |  | ACType |  |  |  | ACType |  |  | M | AC Wiring Type | AC wiring type. |  |  | enum16 | [5 empty] | 2
APU 1 | APS | SunSpec | 701 |  | St |  |  |  | St |  |  |  | Operating State | Operating state of the DER. |  |  | enum16 | [5 empty] | 3
APU 1 | APS | SunSpec | 701 |  | InvSt |  |  |  | InvSt |  |  |  | Inverter State | Enumerated value. Inverter state. |  |  | enum16 | [5 empty] | 4
APU 1 | APS | SunSpec | 701 |  | ConnSt |  |  |  | ConnSt |  |  |  | Grid Connection State | Grid connection state of the DER. |  |  | enum16 | [5 empty] | 5
APU 1 | APS | SunSpec | 701 |  | Alrm |  |  |  | Alrm |  |  |  | Alarm Bitfield | Active alarms for the DER. |  |  | bitfield32 | [5 empty] | 6
APU 1 | APS | SunSpec | 701 |  | Alrm | 0 | GROUND_FAULT | [5 empty] | Ground Fault
APU 1 | APS | SunSpec | 701 |  | Alrm | 1 | DC_OVER_VOLT | [5 empty] | DC Over Voltage
APU 1 | APS | SunSpec | 701 |  | Alrm | 2 | AC_DISCONNECT | [5 empty] | AC Disconnect Open
APU 1 | APS | SunSpec | 701 |  | Alrm | 3 | DC_DISCONNECT | [5 empty] | DC Disconnect Open
APU 1 | APS | SunSpec | 701 |  | Alrm | 4 | GRID_DISCONNECT | [5 empty] | Grid Disconnect
APU 1 | APS | SunSpec | 701 |  | Alrm | 5 | CABINET_OPEN | [5 empty] | Cabinet Open
APU 1 | APS | SunSpec | 701 |  | Alrm | 6 | MANUAL_SHUTDOWN | [5 empty] | Manual Shutdown
APU 1 | APS | SunSpec | 701 |  | Alrm | 7 | OVER_TEMP | [5 empty] | Over Temperature
APU 1 | APS | SunSpec | 701 |  | Alrm | 8 | OVER_FREQUENCY | [5 empty] | Frequency Above Limit
APU 1 | APS | SunSpec | 701 |  | Alrm | 9 | UNDER_FREQUENCY | [5 empty] | Frequency Under Limit
APU 1 | APS | SunSpec | 701 |  | Alrm | 10 | AC_OVER_VOLT | [5 empty] | AC Voltage Above Limit
APU 1 | APS | SunSpec | 701 |  | Alrm | 11 | AC_UNDER_VOLT | [5 empty] | AC Voltage Under Limit
APU 1 | APS | SunSpec | 701 |  | Alrm | 12 | BLOWN_STRING_FUSE | [5 empty] | Blown String Fuse On Input
APU 1 | APS | SunSpec | 701 |  | Alrm | 13 | UNDER_TEMP | [5 empty] | Under Temperature
APU 1 | APS | SunSpec | 701 |  | Alrm | 14 | MEMORY_LOSS | [5 empty] | Generic Memory Or Communication Error (Internal)
APU 1 | APS | SunSpec | 701 |  | Alrm | 15 | HW_TEST_FAILURE | [5 empty] | Hardware Test Failure
APU 1 | APS | SunSpec | 701 |  | Alrm | 16 | MANUFACTURER_ALRM | [5 empty] | Manufacturer Alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
APU 1 | APS | SunSpec | 701 |  | DERMode | [7 empty] | DER Operational Characteristics | Current operational characteristics of the DER. |  |  | bitfield32 | [5 empty] | 8
APU 1 | APS | SunSpec | 701 |  | DERMode | 0 | GRID_FOLLOWING | [5 empty] | Grid Following | The DER is operating as part of a larger grid.
APU 1 | APS | SunSpec | 701 |  | DERMode | 1 | GRID_FORMING | [5 empty] | Grid Forming | The DER is providing the grid.
APU 1 | APS | SunSpec | 701 |  | DERMode | 2 | PV_CLIPPED | [5 empty] | PV Output Clipped | The PV output is clipped.
APU 1 | APS | SunSpec | 701 |  | W |  |  |  | W | APU Active Power Total | APU Active Power Total |  | Active Power | Total active power. | INT16 |  | int16 | kW/10 | 1000 | W | 1 | 1 | 10 | 8402 | 200 | INPUT_REGISTER | W_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VA | [7 empty] | Apparent Power | Total apparent power. |  |  | int16 |  |  | VA |  |  | 11
APU 1 | APS | SunSpec | 701 |  | Var |  |  |  | VA | APU Reactive Power Total | APU Reactive Power Total |  | Reactive Power | Total reactive power. | INT16 |  | int16 | kvar/10 | 1000 | Var | 1 | 1 | 12 | 8406 | 200 | INPUT_REGISTER | Var_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | PF | [7 empty] | Power Factor | Power factor. |  |  | uint16 | [5 empty] | 13
APU 1 | APS | SunSpec | 701 |  | A | [7 empty] | Total AC Current | Total AC current. |  |  | int16 |  |  | A |  |  | 14
APU 1 | APS | SunSpec | 701 |  | LLV | [7 empty] | Voltage LL | Line to line AC voltage as an average of active phases. |  |  | uint16 |  |  | V |  |  | 15
APU 1 | APS | SunSpec | 701 |  | LNV | [7 empty] | Voltage LN | Line to neutral AC voltage as an average of active phases. |  |  | uint16 |  |  | V |  |  | 16
APU 1 | APS | SunSpec | 701 |  | Hz | [7 empty] | Frequency | AC frequency. | UNIT16 |  | uint32 | Hz/1000 | 1 | Hz | 1 | 2 | 17 | 8398 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhInj |  |  |  | TotWhInj | APU Energy Counter Positive Total | APS Energy Counter Positive Total |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4). | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 19 | 8429 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhAbs |  |  |  | TotWhAbs | APU Energy Counter Negative Total | APU Energy Counter Negative Total |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3). | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 23 | 8437 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotVarhInj | [7 empty] | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2). |  |  | uint64 |  |  | Varh |  |  | 27
APU 1 | APS | SunSpec | 701 |  | TotVarhAbs | [7 empty] | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4). |  |  | uint64 |  |  | Varh |  |  | 31
APU 1 | APS | SunSpec | 701 |  | TmpAmb |  |  |  | TmpAmb | Ambient Temperature | Ambient Temperature |  | Ambient Temperature | Ambient temperature. |  |  | int16 |  |  | C |  |  | 35
APU 1 | APS | SunSpec | 701 |  | TmpCab |  |  |  | TmpCab | APU 1 PCB Temperature | APU 1 PCB Temperature |  | Cabinet Temperature | Cabinet temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 36 | 8496 | 200 | INPUT_REGISTER | Tmp_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TmpSnk | [7 empty] | Heat Sink Temperature | Heat sink temperature. |  |  | int16 |  |  | C |  |  | 37
APU 1 | APS | SunSpec | 701 |  | TmpTrns | [7 empty] | Transformer Temperature | Transformer temperature. |  |  | int16 |  |  | C |  |  | 38
APU 1 | APS | SunSpec | 701 |  | TmpSw |  |  |  | TmpSw | APU 1 IGBT Temperature L1 | APU 1 IGBT Temperature L1 |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 39 | 8414 | 200 | INPUT_REGISTER | Tmp_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TmpSw |  |  |  | TmpSw | APU 1 IGBT Temperature L2 | APU 1 IGBT Temperature L2 |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 39 | 8415 | 200 | INPUT_REGISTER | Tmp_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TmpSw |  |  |  | TmpSw | APU 1 IGBT Temperature L3 | APU 1 IGBT Temperature L3 |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 39 | 8416 | 200 | INPUT_REGISTER | Tmp_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TmpOt |  |  |  | TmpOt | APU 1 Inductor Temperature | APU 1 Inductor Temperature |  | Other Temperature | Other temperature. | INT16 |  | int16 | C/10 | 1 | C | 1 | 1 | 40 | 8413 | 200 | INPUT_REGISTER | Tmp_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | WL1 |  |  |  | WL1 | APU Active Power L1 | APU Active Power L1 |  | Watts L1 | Active power L1. | INT16 |  | int16 | kW/10 | 1000 | W | 1 | 1 | 41 | 8403 | 200 | INPUT_REGISTER | W_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VAL1 | [7 empty] | VA L1 | Apparent power L1. |  |  | int16 |  |  | VA |  |  | 42
APU 1 | APS | SunSpec | 701 |  | VarL1 |  |  |  | VarL1 | APU 1 Reactive Power L1 | APU 1 Reactive Power L1 |  | Var L1 | Reactive power L1. | INT16 |  | int16 | kvar/10 | 1000 | Var | 1 | 1 | 43 | 8407 | 200 | INPUT_REGISTER | Var_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | PFL1 | [7 empty] | PF L1 | Power factor phase L1. |  |  | uint16 | [5 empty] | 44
APU 1 | APS | SunSpec | 701 |  | AL1 |  |  |  | AL1 | APU 1 Grid Current L1 | APU 1 Grid Current L1 |  | Amps L1 | Current phase L1. | UNIT16 |  | int16 | A/10 | 1 | A | 1 | 1 | 45 | 8399 | 200 | INPUT_REGISTER | A_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL1L2 | [7 empty] | Phase Voltage L1-L2 | Phase voltage L1-L2. | UNIT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 46 | 8395 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL1 | [7 empty] | Phase Voltage L1-N | Phase voltage L1-N. | UNIT16 |  | uint16 | V | 0.1 | V | 1 | 1 | 47 | 8392 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhInjL1 |  |  |  | TotWhInjL1 | APU 1 Energy Counter Positive L1 | APU 1 Energy Counter Positive L1 |  | Total Watt-Hours Inj L1 | Total active energy injected L1. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 48 | 8431 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhAbsL1 |  |  |  | TotWhAbsL1 |  |  |  | Total Watt-Hours Abs L1 | Total active energy absorbed L1. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 52 | 8439 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotVarhInjL1 | [7 empty] | Total Var-Hours Inj L1 | Total reactive energy injected L1. |  |  | uint64 |  |  | Varh |  |  | 56
APU 1 | APS | SunSpec | 701 |  | TotVarhAbsL1 | [7 empty] | Total Var-Hours Abs L1 | Total reactive energy absorbed L1. |  |  | uint64 |  |  | Varh |  |  | 60
APU 1 | APS | SunSpec | 701 |  | WL2 |  |  |  | WL2 | APU 1 Active Power L2 | APU 1 Active Power L2 |  | Watts L2 | Active power L2. | INT16 |  | int16 | kW/10 | 1000 | W | 1 | 1 | 64 | 8404 | 200 | INPUT_REGISTER | W_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VAL2 | [7 empty] | VA L2 | Apparent power L2. |  |  | int16 |  |  | VA |  |  | 65
APU 1 | APS | SunSpec | 701 |  | VarL2 |  |  |  | VarL2 | APU 1 Reactive Power L2 | APU 1 Reactive Power L2 |  | Var L2 | Reactive power L2. | INT16 |  | int16 | kvar/10 | 1000 | Var | 1 | 1 | 66 | 8408 | 200 | INPUT_REGISTER | Var_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | PFL2 | [7 empty] | PF L2 | Power factor L2. |  |  | uint16 | [5 empty] | 67
APU 1 | APS | SunSpec | 701 |  | AL2 |  |  |  | AL2 | APU 1 Grid Current L2 | APU 1 Grid Current L2 |  | Amps L2 | Current L2. | UNIT16 |  | int16 | A/10 | 1 | A | 1 | 1 | 68 | 8400 | 200 | INPUT_REGISTER | A_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL2L3 | [7 empty] | Phase Voltage L2-L3 | Phase voltage L2-L3. | UNIT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 69 | 8396 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL2 | [7 empty] | Phase Voltage L2-N | Phase voltage L2-N. | UNIT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 70 | 8393 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhInjL2 |  |  |  | TotWhInjL2 | APU 1 Energy Counter Positive L2 | APU 1 Energy Counter Positive L2 |  | Total Watt-Hours Inj L2 | Total active energy injected L2. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 71 | 8433 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhAbsL2 |  |  |  | TotWhAbsL2 | APU 1 Energy Counter Negative L2 | APU 1 Energy Counter Negative L2 |  | Total Watt-Hours Abs L2 | Total active energy absorbed L2. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 75 | 8441 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotVarhInjL2 | [7 empty] | Total Var-Hours Inj L2 | Total reactive energy injected L2. |  |  | uint64 |  |  | Varh |  |  | 79
APU 1 | APS | SunSpec | 701 |  | TotVarhAbsL2 | [7 empty] | Total Var-Hours Abs L2 | Total reactive energy absorbed L2. |  |  | uint64 |  |  | Varh |  |  | 83
APU 1 | APS | SunSpec | 701 |  | WL3 |  |  |  | WL3 | APU 1 Active Power L3 | APU 1 Active Power L3 |  | Watts L3 | Active power L3. | INT16 |  | int16 | kW/10 | 1000 | W | 1 | 1 | 87 | 8405 | 200 | INPUT_REGISTER | W_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VAL3 | [7 empty] | VA L3 | Apparent power L3. |  |  | int16 |  |  | VA |  |  | 88
APU 1 | APS | SunSpec | 701 |  | VarL3 |  |  |  | VarL3 | APU 1 Reactive Power L3 | APU 1 Reactive Power L3 |  | Var L3 | Reactive power L3. | INT16 |  | int16 | kvar/10 | 1000 | Var | 1 | 1 | 89 | 8409 | 200 | INPUT_REGISTER | Var_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | PFL3 | [7 empty] | PF L3 | Power factor L3. |  |  | uint16 | [5 empty] | 90
APU 1 | APS | SunSpec | 701 |  | AL3 |  |  |  | AL3 | APU 1 Grid Current L3 | APU 1 Grid Current L3 |  | Amps L3 | Current L3. | UNIT16 |  | int16 | A/10 | 1 | A | 1 | 1 | 91 | 8401 | 200 | INPUT_REGISTER | A_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL3L1 | [7 empty] | Phase Voltage L3-L1 | Phase voltage L3-L1. | UNIT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 92 | 8397 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | VL3 | [7 empty] | Phase Voltage L3-N | Phase voltage L3-N. | UNIT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 93 | 8394 | 200 | INPUT_REGISTER | V_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhInjL3 |  |  |  | TotWhInjL3 | APU 1 Energy Counter Positive L3 | APU 1 Energy Counter Positive L3 |  | Total Watt-Hours Inj L3 | Total active energy injected L3. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 94 | 8435 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotWhAbsL3 |  |  |  | TotWhAbsL3 | APU 1 Energy Counter Negative L3 | APU1 Energy Counter Negative L3 |  | Total Watt-Hours Abs L3 | Total active energy absorbed L3. | UNIT32 |  | uint64 | kWh/10 | 1000 | Wh | 2 | 4 | 98 | 8443 | 200 | INPUT_REGISTER | TotWh_SF |  |  | RO
APU 1 | APS | SunSpec | 701 |  | TotVarhInjL3 | [7 empty] | Total Var-Hours Inj L3 | Total reactive energy injected L3. |  |  | uint64 |  |  | Varh |  |  | 102
APU 1 | APS | SunSpec | 701 |  | TotVarhAbsL3 | [7 empty] | Total Var-Hours Abs L3 | Total reactive energy absorbed L3. |  |  | uint64 |  |  | Varh |  |  | 106
APU 1 | APS | SunSpec | 701 |  | ThrotPct | [7 empty] | Throttling In Pct | Throttling in pct of maximum active power. |  |  | uint16 |  |  | Pct |  |  | 110
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | [7 empty] | Throttle Source Information | Active throttling source. |  |  | bitfield32 | [5 empty] | 111
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 0 | MAX_W
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 1 | FIXED_W
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 2 | FIXED_VAR
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 3 | FIXED_PF
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 4 | VOLT_VAR
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 5 | FREQ_WATT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 6 | DYN_REACT_CURR
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 7 | LVRT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 8 | HVRT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 9 | WATT_VAR
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 10 | VOLT_WATT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 11 | SCHEDULED
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 12 | LFRT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 13 | HFRT
APU 1 | APS | SunSpec | 701 |  | ThrotSrc | 14 | DERATED
APU 1 | APS | SunSpec | 701 |  | A_SF | [7 empty] | Current Scale Factor | Current scale factor. |  |  | sunssf | [5 empty] | 113
APU 1 | APS | SunSpec | 701 |  | V_SF | [7 empty] | Voltage Scale Factor | Voltage scale factor. |  |  | sunssf | [5 empty] | 114
APU 1 | APS | SunSpec | 701 |  | Hz_SF | [7 empty] | Frequency Scale Factor | Frequency scale factor. |  |  | sunssf | [5 empty] | 115
APU 1 | APS | SunSpec | 701 |  | W_SF | [7 empty] | Active Power Scale Factor | Active power scale factor. |  |  | sunssf | [5 empty] | 116
APU 1 | APS | SunSpec | 701 |  | PF_SF | [7 empty] | Power Factor Scale Factor | Power factor scale factor. |  |  | sunssf | [5 empty] | 117
APU 1 | APS | SunSpec | 701 |  | VA_SF | [7 empty] | Apparent Power Scale Factor | Apparent power scale factor. |  |  | sunssf | [5 empty] | 118
APU 1 | APS | SunSpec | 701 |  | Var_SF | [7 empty] | Reactive Power Scale Factor | Reactive power scale factor. |  |  | sunssf | [5 empty] | 119
APU 1 | APS | SunSpec | 701 |  | TotWh_SF | [7 empty] | Active Energy Scale Factor | Active energy scale factor. |  |  | sunssf | [5 empty] | 120
APU 1 | APS | SunSpec | 701 |  | TotVarh_SF | [7 empty] | Reactive Energy Scale Factor | Reactive energy scale factor. |  |  | sunssf | [5 empty] | 121
APU 1 | APS | SunSpec | 701 |  | Tmp_SF | [7 empty] | Temperature Scale Factor | Frequency scale factor. |  |  | sunssf | [5 empty] | 122
APU 1 | APS | SunSpec | 701 |  | MnAlrmInfo | [7 empty] | Manufacturer Alarm Info | Manufacturer alarm information. |  |  | string |  |  |  |  | 32 | 123
APU 1 | APS | SunSpec | 121 |  | VMax |  |  |  | VMax | APU 1 Applied 1 DC Voltage Maximum | APU 1 Applied 1 DC Voltage Maximum |  | VMin | Setpoint for maximum voltage. | UINT16 |  | UNIT16 | V/10 | 1 | V | 1 | 1 | 5 | 24604 | 30 | HOLDING_REGISTER | VMinMax_SF |  |  | RO
APU 1 | APS | SunSpec | 121 |  | VMin |  |  |  | VMin | APU 1 Applied DC Voltage Minimum | APU 1 Applied DC Voltage Minimum |  | VAMax | Setpoint for minimum voltage. | UINT16 |  | UNIT16 | V/10 | 1 | V | 1 | 1 | 6 | 24605 | 30 | HOLDING_REGISTER | VMinMax_SF |  |  | RO
APU 1 | APS | SunSpec | 704 |  | WSet |  |  |  | WSet | APU 1 Active Power Set point | APU 1 Active Power Set point |  | Active Power Setpoint (W) | Active power setting value in watts. | INT16 |  | INT32 | KW/10 | 1000 | W | 1 | 2 | 24 | 24596 | 30 | HOLDING_REGISTER | WSet_SF |  |  | RO
APU 1 | APS | SunSpec | 704 |  | VarSet |  |  |  | VarSet | APU 1 Reactive Power Set Point | APU 1 Reactive Power Set Point |  | Reactive Power Setpoint (Vars) | Reactive power setting value in vars. | INT16 |  | INT32 | KVAr/10 | 1000 | Var | 1 | 2 | 38 | 24600 | 30 | HOLDING_REGISTER | VarSet_SF |  |  | RO
APU 1 | APS | SunSpec | 704 |  | WMaxLimPct |  |  |  | WMaxLimPct | APU 1 Applied Active Power Limit | APU 1 Applied Active Power Limit |  | Limit Max Power Pct Setpoint | Limit maximum active power percent value. | INT16 |  | unit16 | KW |  | % | 1 | 1 | 15 | 8417 | 200 | INPUT_REGISTER | WMaxLimPct_SF |  |  | RO
APU 1 | APS | SunSpec | 714 |  | DCA |  |  |  | DCA | APU 1 DC Current | APU 1 DC Current |  | DC Current | Total DC current for all ports. | INT16 |  | int16 | A/10 | 1 | A | 1 | 1 | 5 | 8411 | 200 | INPUT_REGISTER | DCA_SF |  |  | RO
APU 1 | APS | SunSpec | 714 |  | DCW |  |  |  | DCW | APU 1 DC Power | APU 1 DC Power |  | DC Power | Total DC power for all ports. | INT16 |  | int16 | Kw/10 | 1000 | W | 1 | 1 | 6 | 8412 | 200 | INPUT_REGISTER | DCW_SF |  |  | RO
APU 1 | APS | SunSpec | 714 |  | DCV |  |  |  | DCV | APU 1 DC Voltage | APU 1 DC Voltage |  |  | APU 1 DC Voltage | INT16 |  | uint16 | V/10 | 1 | V | 1 | 1 | 11 | 8410 | 200 | INPUT_REGISTER | DCV_SF |  |  | RO
APU 1 | APS | SunSpec | 122 |  | Ris |  |  |  | Ris | APU 1 Insulation Resistance | APU 1 Insulation Resistance |  |  | APU 1 Insulation Resistance | UINT16 |  | unit16 | kΩ/10 | 1 | Kohm | 1 | 1 | 44 | 8497 | 200 | INPUT_REGISTER | Ris_SF |  |  | RO
APU 1 | APS | SunSpec | 715 |  | DERHb |  |  |  | DERHb | APU 1 Heartbeat | APU 1 Heartbeat |  | DER Heartbeat | Value is incremented every second by the DER with periodic resets to zero. | UINT16 |  | UNIT32 |  |  |  | 1 | 2 | 3 | 24612 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1AppliedVArPowerLim | APU 1 Applied Reactive Power Limit | APU 1 Applied Reactive Power Limit |  |  | APU 1 Applied Reactive Power Limit | INT16 |  |  | KVAr/10 | 1 |  | 1 |  |  | 8421 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1AppliedDCVoltMax | APU 1 Applied DC Voltage Maximum | APU 1 Applied DC Voltage Maximum |  |  | APU 1 Applied DC Voltage Maximum | INT16 |  |  | V/10 | 1 |  | 1 |  |  | 8425 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1AppliedDCVoltMin | APU 1 Applied DC Voltage Minimum | APU 1 Applied DC Voltage Minimum |  |  | APU 1 Applied DC Voltage Minimum | INT16 |  |  | V/10 | 1 |  | 1 |  |  | 8426 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1AppliedPostivDCCurrentLim | APU 1 Applied Positive DC Current Limit | APU 1 Applied Positive DC Current Limit |  |  | APU 1 Applied Positive DC Current Limit | INT16 |  |  | A/10 | 1 |  | 1 |  |  | 8427 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1AppliedNegetivDCCurrentLim | APU 1 Applied Negative DC Current Limit | APU 1 Applied Negative DC Current Limit |  |  | APU 1 Applied Negative DC Current Limit | INT16 |  |  | A/10 | 1 |  | 1 |  |  | 8428 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1StartCountdown | APU 1 Start Countdown | APU 1 Start Countdown |  |  | APU 1 Start Countdown | UINT16 |  |  | s | 1 |  | 1 |  |  | 8494 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Humidity | APU 1 Humidity | APU 1 Humidity |  |  | APU 1 Humidity | UINT16 |  |  | %rh/10 | 1 |  | 1 |  |  | 8495 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1LeakageCapacitence | APU 1 Leakage Capacitance | APU 1 Leakage Capacitance |  |  | APU 1 Leakage Capacitance | UINT16 |  |  | μF/10 | 1 |  | 1 |  |  | 8498 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1FirmwareVer | APU 1 Firmware Version | APU 1 Firmware Version |  |  | APU 1 Firmware Version | UINT16 |  |  |  | 1 |  | 1 |  |  | 8499 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1DCinputVolt | APU 1 DC Input Voltage | APU 1 DC Input Voltage |  |  | APU 1 DC Input Voltage | UINT16 |  |  | V/10 | 1 |  | 1 |  |  | 10060 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosDCCurrentLim | APU 1 Positive DC Current Limit | APU 1 Positive DC Current Limit |  |  | APU 1 Positive DC Current Limit | INT16 |  |  | A/10 | 1 |  | 1 |  |  | 24606 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegDCCurrentLim | APU 1 Negative DC Current Limit | APU 1 Negative DC Current Limit |  |  | APU 1 Negative DC Current Limit | INT16 |  |  | A/11 | 1 |  | 1 |  |  | 24607 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1IslandVoltSetPoint | APU 1 Island Voltage Set Point | APU 1 Island Voltage Set Point |  |  | APU 1 Island Voltage Set Point | UINT16 |  |  | V/10 | 1 |  | 1 |  |  | 24608 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1IslandFrSetPoint | APU 1 Island Frequency Set Point | APU 1 Island Frequency Set Point |  |  | APU 1 Island Frequency Set Point | UINT16 |  |  | Hz/1000 | 1 |  | 1 |  |  | 24609 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrorRst | APU 1 Error Reset | APU 1 Error Reset |  |  | APU 1 Error Reset | UINT16 | [5 empty] | 1 |  |  | 24611 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount1 | APU 1 Positiv Ah Counter 1 | APU 1 Positiv Ah Counter 1 |  |  | APU 1 Positiv Ah Counter 1 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10000 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount1 | APU 1 Negitive Ah Counter 1 | APU 1 Negitive Ah Counter 1 |  |  | APU 1 Negitive Ah Counter 1 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10002 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current1 | APU 1 Current 1 | APU 1 Current 1 |  |  | APU 1 Current 1 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10004 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount2 | APU 1 Positiv Ah Counter 2 | APU 1 Positiv Ah Counter 2 |  |  | APU 1 Positiv Ah Counter 2 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10005 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount2 | APU 1 Negitive Ah Counter 2 | APU 1 Negitive Ah Counter 2 |  |  | APU 1 Negitive Ah Counter 2 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10007 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current2 | APU 1 Current 2 | APU 1 Current 2 |  |  | APU 1 Current 2 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10009 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount3 | APU 1 Positiv Ah Counter 3 | APU 1 Positiv Ah Counter 3 |  |  | APU 1 Positiv Ah Counter 3 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10010 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount3 | APU 1 Negitive Ah Counter 3 | APU 1 Negitive Ah Counter 3 |  |  | APU 1 Negitive Ah Counter 3 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10012 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current3 | APU 1 Current 3 | APU 1 Current 3 |  |  | APU 1 Current 3 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10014 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount4 | APU 1 Positiv Ah Counter 4 | APU 1 Positiv Ah Counter 4 |  |  | APU 1 Positiv Ah Counter 4 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10015 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount4 | APU 1 Negitive Ah Counter 4 | APU 1 Negitive Ah Counter 4 |  |  | APU 1 Negitive Ah Counter 4 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10017 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current4 | APU 1 Current 4 | APU 1 Current 4 |  |  | APU 1 Current 4 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10019 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount5 | APU 1 Positiv Ah Counter 5 | APU 1 Positiv Ah Counter 5 |  |  | APU 1 Positiv Ah Counter 5 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10020 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount5 | APU 1 Negitive Ah Counter 5 | APU 1 Negitive Ah Counter 5 |  |  | APU 1 Negitive Ah Counter 5 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10022 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current5 | APU 1 Current 5 | APU 1 Current 5 |  |  | APU 1 Current 5 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10024 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount6 | APU 1 Positiv Ah Counter 6 | APU 1 Positiv Ah Counter 6 |  |  | APU 1 Positiv Ah Counter 6 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10025 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount6 | APU 1 Negitive Ah Counter 6 | APU 1 Negitive Ah Counter 6 |  |  | APU 1 Negitive Ah Counter 6 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10027 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current6 | APU 1 Current 6 | APU 1 Current 6 |  |  | APU 1 Current 6 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10029 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount7 | APU 1 Positiv Ah Counter 7 | APU 1 Positiv Ah Counter 7 |  |  | APU 1 Positiv Ah Counter 7 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10030 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount7 | APU 1 Negitive Ah Counter 7 | APU 1 Negitive Ah Counter 7 |  |  | APU 1 Negitive Ah Counter 7 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10032 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current7 | APU 1 Current 7 | APU 1 Current 7 |  |  | APU 1 Current 7 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10034 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount8 | APU 1 Positiv Ah Counter 8 | APU 1 Positiv Ah Counter 8 |  |  | APU 1 Positiv Ah Counter 8 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10035 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount8 | APU 1 Negitive Ah Counter 8 | APU 1 Negitive Ah Counter 8 |  |  | APU 1 Negitive Ah Counter 8 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10037 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current8 | APU 1 Current 8 | APU 1 Current 8 |  |  | APU 1 Current 8 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10039 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount9 | APU 1 Positiv Ah Counter 9 | APU 1 Positiv Ah Counter 9 |  |  | APU 1 Positiv Ah Counter 9 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10040 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount9 | APU 1 Negitive Ah Counter 9 | APU 1 Negitive Ah Counter 9 |  |  | APU 1 Negitive Ah Counter 9 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10042 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current9 | APU 1 Current 9 | APU 1 Current 9 |  |  | APU 1 Current 9 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10044 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount10 | APU 1 Positiv Ah Counter 10 | APU 1 Positiv Ah Counter 10 |  |  | APU 1 Positiv Ah Counter 10 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10045 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount10 | APU 1 Negitive Ah Counter 10 | APU 1 Negitive Ah Counter 10 |  |  | APU 1 Negitive Ah Counter 10 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10047 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current10 | APU 1 Current 10 | APU 1 Current 10 |  |  | APU 1 Current 10 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10049 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount11 | APU 1 Positiv Ah Counter 11 | APU 1 Positiv Ah Counter 11 |  |  | APU 1 Positiv Ah Counter 11 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10050 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount11 | APU 1 Negitive Ah Counter 11 | APU 1 Negitive Ah Counter 11 |  |  | APU 1 Negitive Ah Counter 11 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10052 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current11 | APU 1 Current 11 | APU 1 Current 11 |  |  | APU 1 Current 11 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10054 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1PosAhCount12 | APU 1 Positiv Ah Counter 12 | APU 1 Positiv Ah Counter 12 |  |  | APU 1 Positiv Ah Counter 12 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10055 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1NegAhCount12 | APU 1 Negitive Ah Counter 12 | APU 1 Negitive Ah Counter 12 |  |  | APU 1 Negitive Ah Counter 12 | UINT32 |  |  | Ah/100 | 1 |  | 2 |  |  | 10057 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1Current12 | APU 1 Current 12 | APU 1 Current 12 |  |  | APU 1 Current 12 | UINT16 |  |  | A/100 | 1 |  | 1 |  |  | 10059 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes | APU1 Error Code1 | APU1 Error Code1 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8445 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1OpMod | APU 1 OPEARTING MODES | APU 1 Operating Modes |  |  | APU 1 Operating Modes | UINT16 | [5 empty] | 1 |  |  | 24610 | 30 | HOLDING_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1OpSt | APU 1 Operating Status | APU 1 Operating State |  |  | APU 1 Operating State | UINT16 | [5 empty] | 1 |  |  | 8493 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes2 | APU1 Error Code2 | APU1 Error Code2 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8446 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes3 | APU1 Error Code3 | APU1 Error Code3 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8447 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes4 | APU1 Error Code4 | APU1 Error Code4 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8448 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes5 | APU1 Error Code5 | APU1 Error Code5 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8449 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes6 | APU1 Error Code6 | APU1 Error Code6 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8450 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes7 | APU1 Error Code7 | APU1 Error Code7 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8451 | 200 | INPUT_REGISTER |  |  |  | RO
APU 1 | APS | SunSpec | 64092 | [5 empty] | APU1ErrCodes8 | APU1 Error Code8 | APU1 Error Code8 |  |  | APU1 Error Code1 | UINT16 | [5 empty] | 1 |  |  | 8452 | 200 | INPUT_REGISTER |  |  |  | RO

## APS_ENUM
Resource Set | Enum name | Sunspec Enum Value | Sunspec Enum Name | Vendor Enum name | Vendor Enum value | Remarks
SunSpec | ACType
| ACType | 0 | SINGLE_PHASE
| ACType | 1 | SPLIT_PHASE
| ACType | 2 | THREE_PHASE
SunSpec | St
| St | 0 | OFF
| St | 1 | ON
SunSpec | InvSt
| InvSt | 0 | OFF
| InvSt | 1 | SLEEPING
| InvSt | 2 | STARTING
| InvSt | 3 | MPPT
| InvSt | 4 | THROTTLED
| InvSt | 5 | SHUTTING_DOWN
| InvSt | 6 | FAULT
| InvSt | 7 | STANDBY
SunSpec | ConnSt
| ConnSt | 0 | DISCONNECTED
| ConnSt | 1 | CONNECTED
APS | APS Error Code 1 |  |  | APS Error Code 1
| APS Error Code 1 |  |  | MODBUS _TCP_VALUE_OUT OF RANGE | 1
| APS Error Code 1 |  |  | CONFIGURATION_LOAD/SLAVE | 2
| APS Error Code 1 |  |  | APU 1/2 COOLING_FLUID_LOW | 3
| APS Error Code 1 |  |  | APU 3/4 COOLING_FLUID_LOW | 4
| APS Error Code 1 |  |  | NO_ENABLE_SIGNAL | 5
| APS Error Code 1 |  |  | NO_SUPPLY_VOLTAGE | 6
| APS Error Code 1 |  |  | MEDIUM_VOLTAGE_SWITCHGEAR_OFF | 7
| APS Error Code 1 |  |  | DI_TEMP_NOT OK (OPTIONAL_HEATING) | 8
| APS Error Code 1 |  |  | DI_MEDIUM_VOLTAGE_TRANSFORMER_ERROR | 9
| APS Error Code 1 |  |  | APU 1/2 WATER_PUMPING_SWITCHING_CYCLES | 10
| APS Error Code 1 |  |  | APU 3/4 WATER_PUMPING_SWITCHING_CYCLES | 11
| APS Error Code 1 |  |  | APU 5/6 WATER_PUMPING_SWITCHING_CYCLES | 12
| APS Error Code 1 |  |  | APU 1/2 _AIR_AIR COOLER_SWITCHING_CYCLES | 13
| APS Error Code 1 |  |  | APU 3/4 _AIR_AIR COOLER_SWITCHING_CYCLES | 14
| APS Error Code 1 |  |  | APU 5/6 _AIR_AIR COOLER_SWITCHING_CYCLES | 15
| APS Error Code 1 |  |  | APU 1/2_WATER_AIR COOLER_SWITCHING_CYCLES | 16
| APS Error Code 1 |  |  | APU 3/4_WATER_AIR COOLER_SWITCHING_CYCLES | 17
| APS Error Code 1 |  |  | APU 5/6_WATER_AIR COOLER_SWITCHING_CYCLES | 18
| APS Error Code 1 |  |  | SUPPLY_VOLTAGE_LOW | 19
| APS Error Code 1 |  |  | MODBUS_TCP_TIMEOUT | 20
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 21
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 22
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 23
| APS Error Code 1 |  |  | MEDIUM_VOLTAGE_TRANSFORMER_TEMP_HIGH | 24
| APS Error Code 1 |  |  | APU 5/6_COOLING_FLUID_LOW | 25
| APS Error Code 1 |  |  | ERROR_COUNTER_OVERRUN | 26
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 27
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 28
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 29
| APS Error Code 1 |  |  | APU 1_POWERLINK | 30
| APS Error Code 1 |  |  | APU 2_POWERLINK | 31
| APS Error Code 1 |  |  | APU 3_POWERLINK | 32
| APS Error Code 1 |  |  | APU 4_POWERLINK | 33
| APS Error Code 1 |  |  | APU 5_POWERLINK | 34
| APS Error Code 1 |  |  | APU 6_POWERLINK | 35
| APS Error Code 1 |  |  | APU 1_TYPE_MISMATCH | 36
| APS Error Code 1 |  |  | APU 2_TYPE_MISMATCH | 37
| APS Error Code 1 |  |  | APU 3_TYPE_MISMATCH | 38
| APS Error Code 1 |  |  | APU 4_TYPE_MISMATCH | 39
| APS Error Code 1 |  |  | APU 5_TYPE_MISMATCH | 40
| APS Error Code 1 |  |  | APU 6_TYPE_MISMATCH | 41
| APS Error Code 1 |  |  | APS_UNLICENSED | 42
| APS Error Code 1 |  |  | INTERNAL_CONFIGURATION_NOT_VALID | 43
| APS Error Code 1 |  |  | APU_UPDATE | 44
| APS Error Code 1 |  |  | APMC_BATTERY_MISSING_EMPTY | 45
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 46
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 47
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 48
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 49
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 50
| APS Error Code 1 |  |  | INSULATION _MONITERING_MODE | 51
| APS Error Code 1 |  |  | HW_WIRING_DIAGRAM_NOT_VALID | 52
| APS Error Code 1 |  |  | APU 1/2_DC-LINK_OVERTEMP | 53
| APS Error Code 1 |  |  | APU 3/4_DC-LINK_OVERTEMP | 54
| APS Error Code 1 |  |  | APU 1/2_GRID_MONITORING_CIRCUIT_HW | 55
| APS Error Code 1 |  |  | APU 3/4_GRID_MONITORING_CIRCUIT_HW | 56
| APS Error Code 1 |  |  | ERR_THRESH_DEHUMIDIFIER | 57
| APS Error Code 1 |  |  | APU 1/2_COMMON_MODE_FILTER | 58
| APS Error Code 1 |  |  | APU 3/4_COMMON_MODE_FILTER | 59
| APS Error Code 1 |  |  | MODB_TIME_APS | 60
| APS Error Code 1 |  |  | MODB_TIME_APU | 61
| APS Error Code 1 |  |  | MODB_TIME_APU | 62
| APS Error Code 1 |  |  | MODB_TIME_APU | 63
| APS Error Code 1 |  |  | MODB_TIME_APU | 64
| APS Error Code 1 |  |  | DC_VOLTAGE_LIMIT | 65
| APS Error Code 1 |  |  | DC_VOLTAGE_LIMIT | 66
| APS Error Code 1 |  |  | DC_VOLTAGE_LIMIT | 67
| APS Error Code 1 |  |  | DC_VOLTAGE_LIMIT | 68
| APS Error Code 1 |  |  | APU 1_STRING_OVERCURRENT | 69
| APS Error Code 1 |  |  | APU 2_STRING_OVERCURRENT | 70
| APS Error Code 1 |  |  | APU 3_STRING_OVERCURRENT | 71
| APS Error Code 1 |  |  | APU 4_STRING_OVERCURRENT | 72
| APS Error Code 1 |  |  | LOM_TRANSFERTRIP1_MODE | 73
| APS Error Code 1 |  |  | LOM_TRANSFERTRIP2_MODE | 74
| APS Error Code 1 |  |  | ROCOF> | 75
| APS Error Code 1 |  |  | ROCOF>> | 76
APS | APS Warning Code 1 |  |  | APU 1 / 2 _COOLING _FLUID LOW | 1
| APS Warning Code 1 |  |  | APU 3 / 4_ COOLONG_ FLUIDLOW | 2
| APS Warning Code 1 |  |  | TIME_ SYNCHRONIZATION_failed | 3
| APS Warning Code 1 |  |  | MODBUS_ RTU_ (Display) | 4
| APS Warning Code 1 |  |  | AC _SUGARARRESTER_ TRIPPED | 5
| APS Warning Code 1 |  |  | DC _SUGARARRESTER_ TRIPPED | 6
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 7
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 8
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 9
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 10
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 11
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 12
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 13
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 14
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 15
| APS Warning Code 1 |  |  | APU 1 _ERROR | 22
| APS Warning Code 1 |  |  | APU 2 _ERROR | 23
| APS Warning Code 1 |  |  | APU 3 _ERROR | 24
| APS Warning Code 1 |  |  | APU 4 _ERROR | 25
| APS Warning Code 1 |  |  | APU 5 _ERROR | 26
| APS Warning Code 1 |  |  | APU 6 _ERROR | 27
| APS Warning Code 1 |  |  | APU 5 / 6 _COOLINGFLUID_ LOW | 28
| APS Warning Code 1 |  |  | APU 1 _POWERLINK | 29
| APS Warning Code 1 |  |  | APU 2 _POWERLINK | 30
| APS Warning Code 1 |  |  | APU 3 _POWERLINK | 31
| APS Warning Code 1 |  |  | APU 4 _POWERLINK | 32
| APS Warning Code 1 |  |  | APU 5 _POWERLINK | 33
| APS Warning Code 1 |  |  | APU 6 _POWERLINK | 34
| APS Warning Code 1 |  |  | POWER_ LIMIT_ TRANSFORMER | 35
| APS Warning Code 1 |  |  | POWER_ LIMIT_ AMBIENT | 36
| APS Warning Code 1 |  |  | APU 1_ ERROR_ COUNTER_ OVER_RUN | 37
| APS Warning Code 1 |  |  | APU 2_ ERROR_ COUNTER_ OVER_RUN | 38
| APS Warning Code 1 |  |  | APU 3_ ERROR_ COUNTER_ OVER_RUN | 39
| APS Warning Code 1 |  |  | APU 4_ ERROR_ COUNTER_ OVER_RUN | 40
| APS Warning Code 1 |  |  | APU 5_ ERROR_ COUNTER_ OVER_RUN | 41
| APS Warning Code 1 |  |  | APU 6_ ERROR_ COUNTER_ OVER_RUN | 42
| APS Warning Code 1 |  |  | APU_ IN_ MANUAL_ MODE | 43
| APS Warning Code 1 |  |  | COOLING_IN_ MANUAL_ MODE | 44
| APS Warning Code 1 |  |  | HEATING_ IN_ MANUAL_ MODE | 45
| APS Warning Code 1 |  |  | APU _IN_ SERVICE_ MODE | 46
| APS Warning Code 1 |  |  | LOG_ SAMPLES_ LOST | 47
| APS Warning Code 1 |  |  | APU 1 / 2_ CURRENT_ MEASUREMENT | 48
| APS Warning Code 1 |  |  | APU 3 / 4 _ CURRENT_ MEASUREMENT | 49
| APS Warning Code 1 |  |  | APU 5 / 6 _ CURRENT_ MEASUREMENT | 50
| APS Warning Code 1 |  |  | APU 1 / 2_ POWER_LINK_ FLICKER | 51
| APS Warning Code 1 |  |  | APU 3 / 4 _ POWER_LINK_ FLICKER | 52
| APS Warning Code 1 |  |  | APU 5 / 6 _ POWER_LINK_ FLICKER | 53
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 54
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 55
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 56
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 57
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 58
| APS Warning Code 1 |  |  | INSULATION _MONITERING_MODE | 59
| APS Warning Code 1 |  |  | USB–DEVICE_ ALMOST_ FULL | 60
| APS Warning Code 1 |  |  | USB–DEVICE_ FULL | 61
| APS Warning Code 1 |  |  | CMB _UP_DATE | 62
| APS Warning Code 1 |  |  | IMD _UP_DATE | 63
| APS Warning Code 1 |  |  | MAX_ MODBUS_TCP _MASTER_ EXEEDED | 64
| APS Warning Code 1 |  |  | ENABLE/DISABLE_APU | 65
| APS Warning Code 1 |  |  | ENABLE/DISABLE_APU | 66
| APS Warning Code 1 |  |  | ENABLE/DISABLE_APU | 67
| APS Warning Code 1 |  |  | ENABLE/DISABLE_APU | 68
| APS Warning Code 1 |  |  | USB–DEVICE_ FAILED | 69
| APS Warning Code 1 |  |  | POWER_ LIMIT_ UNDER_VOLTAGE_ GRID | 70
| APS Warning Code 1 |  |  | APMC – BATTERY _MISSING/EMPTY | 71
| APS Warning Code 1 |  |  | ROCOF> | 72
| APS Warning Code 1 |  |  | ROCOF>> | 73
APS | APS Operating Modes |  |  | APS_OPEARING_MODES
| APS Operating Modes |  |  | ENERGY_ SAVING | 0
| APS Operating Modes |  |  | OFF | 50
| APS Operating Modes |  |  | DC_CONNECT | 200
| APS Operating Modes |  |  | AC_CONNECT | 500
| APS Operating Modes |  |  | AC_CONNECTED _ISLAND_ GRID | 600
| APS Operating Modes |  |  | STATCOM_ MODE_ ACTIVE | 1000
| APS Operating Modes |  |  | CC–CV _MODE_ ACTIVE | 2000
| APS Operating Modes |  |  | CC–CV_ MODE_ ADVANCED | 2001
| APS Operating Modes |  |  | CC–CV + SYNTHETIC_ INERTIA_ MODE _ACTIVE | 2100
| APS Operating Modes |  |  | CC–CV + SYNTHETIC_ INERTIA_ MODE_ ADVANCED | 2101
| APS Operating Modes |  |  | MPPT_ MODE_ ACTIVE | 3000
| APS Operating Modes |  |  | ISLAND_ GRID_ ACTIVE | 4000
APS | APS Operating States |  |  | APS_OPERATING_STATES
| APS Operating States |  |  | ENERGY _SAVING | 0
| APS Operating States |  |  | BOOT_ING | 30
| APS Operating States |  |  | OFF | 50
| APS Operating States |  |  | INIT _DC _CONNECT | 100
| APS Operating States |  |  | WAIT_ DC_ CONNECT | 130
| APS Operating States |  |  | PRE_CHARGE_ DC | 160
| APS Operating States |  |  | DC–CONNECT | 200
| APS Operating States |  |  | CONNECTION_ CONDITIONS_ AC | 300
| APS Operating States |  |  | `` | 330
| APS Operating States |  |  | WAIT_ AC_ CONNECT | 360
| APS Operating States |  |  | PRE_CHARGE_ AC | 400
| APS Operating States |  |  | AC–CONNECT_ ISLAND_ GRID | 500
| APS Operating States |  |  | AC–CONNECT_ ISLAND_ GRID | 600
| APS Operating States |  |  | STATCOM mode active | 1000
| APS Operating States |  |  | STATCOM current limit | 1010
| APS Operating States |  |  | STATCOM power limit | 1020
| APS Operating States |  |  | CC–CV_ MODE_ ACTIVE | 2000
| APS Operating States |  |  | POWER_ LIMIT _INTERFACE | 2010
| APS Operating States |  |  | POWER_ GRADIENT_START_UP | 2020
| APS Operating States |  |  | POWER_ LIMIT P(f) | 2030
| APS Operating States |  |  | CURRENT_ LIMIT_ AC_ FIX | 2110
| APS Operating States |  |  | CURRENT _LIMIT _AC _DYNAMIC | 2120
| APS Operating States |  |  | CURRENT_ LIMIT_ DC_ FIX | 2130
| APS Operating States |  |  | CURRENT _LIMIT _DC _DYNAMIC | 2140
| APS Operating States |  |  | VOLTAGE_ LIMIT_ DC | 2150
| APS Operating States |  |  | MPPT _MODE_ ACTIVE | 3000
| APS Operating States |  |  | MPPT _AC_ POWER_ LIMIT | 3010
| APS Operating States |  |  | MPPT_AC_ CURRENT_ LIMIT | 3020
| APS Operating States |  |  | MPPT_ DC_ VOLTAGE_ LIMIT | 3030
| APS Operating States |  |  | MPPT _CONT_ TRACKING _UP | 3040
| APS Operating States |  |  | MPPT _CONT_ TRACKING _DOWN | 3050
| APS Operating States |  |  | MPPT_ CYCL._ ACTIVE | 3060
| APS Operating States |  |  | MPPT _WAIT_ IDC _MIN | 3070
| APS Operating States |  |  | MPPT _WAIT_ VDC _MIN | 3080
| APS Operating States |  |  | ISLAND_ GRID _START | 4000
| APS Operating States |  |  | ISLAND_ GRID _READY | 4100
| APS Operating States |  |  | LVRT_ SYM | 8100
| APS Operating States |  |  | LVRT_ ASYM_L1 | 8210
| APS Operating States |  |  | LVRT_ ASYM_L2 | 8220
| APS Operating States |  |  | LVRT_ ASYM_L3 | 8230
| APS Operating States |  |  | LVRT_ ASYM2_ L12 | 8310
| APS Operating States |  |  | LVRT _ASYM2 _L23 | 8320
| APS Operating States |  |  | LVRT_ ASYM2_ L31 | 8330
| APS Operating States |  |  | HVRT _SYM | 9100
| APS Operating States |  |  | HVRT_ ASYM_ L1 | 9210
| APS Operating States |  |  | HVRT_ ASYM_ L2 | 9220
| APS Operating States |  |  | HVRT_ ASYM_ L3 | 9230
| APS Operating States |  |  | HVRT_ ASYM2_ L12 | 9310
| APS Operating States |  |  | HVRT _ASYM2_ L23 | 9320
| APS Operating States |  |  | HVRT_ ASYM2_ L31 | 9330
| APS Operating States |  |  | TEST_ BENCH_ MODE | 10000
| APS Operating States |  |  | DIFFERENT_ OPERATING _STATES | 20000

## APU 1_ENUM
Resource Set | Enum name | Sunspec Enum Value | Sunspec Enum Name | Vendor Enum name | Vendor Enum value | Remarks
SunSpec | ACType
| ACType | 0 | SINGLE_PHASE
| ACType | 1 | SPLIT_PHASE
| ACType | 2 | THREE_PHASE
SunSpec | St
| St | 0 | OFF
| St | 1 | ON
SunSpec | InvSt
| InvSt | 0 | OFF
| InvSt | 1 | SLEEPING
| InvSt | 2 | STARTING
| InvSt | 3 | MPPT
| InvSt | 4 | THROTTLED
| InvSt | 5 | SHUTTING_DOWN
| InvSt | 6 | FAULT
| InvSt | 7 | STANDBY
SunSpec | ConnSt
| ConnSt | 0 | DISCONNECTED
| ConnSt | 1 | CONNECTED
APU 1 | APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L1 | 1
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L2 | 2
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L3 | 3
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_INDUCTANCE | 4
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_POS._SW | 5
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_NEG._SW | 6
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_TOTAL_SW | 7
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_POS._SW | 8
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_NEG._SW | 9
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_TOTAL_SW | 10
| APU1 Error Code1 |  |  | OVER_CURRENT_IDC_SW | 11
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L1_SW | 12
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L2_SW | 13
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L3_SW | 14
| APU1 Error Code1 |  |  | RESERVED | 15
| APU1 Error Code1 |  |  | GRID_ROTATION_ERROR | 16
| APU1 Error Code1 |  |  | OVER_FREQUENCY_LEVEL_1 | 17
| APU1 Error Code1 |  |  | OVER_FREQUENCY_LEVEL_2 | 18
| APU1 Error Code1 |  |  | OVER_FREQUENCY_LEVEL_3 | 19
| APU1 Error Code1 |  |  | UNDER_FREQUENCY_LEVEL_1 | 20
| APU1 Error Code1 |  |  | UNDER_FREQUENCY_LEVEL_2 | 21
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL1_LEVEL_1 | 22
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL1_LEVEL_2 | 23
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL1_LEVEL_3 | 24
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL2_LEVEL_1 | 25
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL2_LEVEL_2 | 26
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL2_LEVEL_3 | 27
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL3_LEVEL_1 | 28
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL3_LEVEL_2 | 29
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL3_LEVEL_3 | 30
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL1_LEVEL_1 | 31
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL1_LEVEL_2 | 32
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL2_LEVEL_1 | 33
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL2_LEVEL_2 | 34
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL3_LEVEL_1 | 35
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL3_LEVEL_2 | 36
| APU1 Error Code1 |  |  | DRIVER_L1 | 37
| APU1 Error Code1 |  |  | DRIVER_L2 | 38
| APU1 Error Code1 |  |  | DRIVER_L3 | 39
| APU1 Error Code1 |  |  | OVER_CURRENT_IDC_HW | 40
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L1_HW | 41
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L2_HW | 42
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L3_HW | 43
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_HW | 44
| APU1 Error Code1 |  |  | PWM_ERROR | 45
| APU1 Error Code1 |  |  | SUPPLY_ERROR | 46
| APU1 Error Code1 |  |  | SUPPLY_ERROR_DELAYED | 47
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_NEG._HW | 48
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_NEG._HW | 49
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_POS._HW | 50
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_POS._HW | 51
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_TOTAL_HW | 52
| APU1 Error Code1 |  |  | SUPPLY_ERROR_15V_NEG._SW | 53
| APU1 Error Code1 |  |  | SUPPLY_ERROR_15V_POS._SUM._SW | 54
| APU1 Error Code1 |  |  | SUPPLY_ERROR_15V_DIG_POS._SW | 55
| APU1 Error Code1 |  |  | SUPPLY_ERROR_24V_DRIVER_POS._SW | 56
| APU1 Error Code1 |  |  | SUPPLY_ERROR_24V_NEG._SW | 57
| APU1 Error Code1 |  |  | SUPPLY_ERROR_24V_POS._SW | 58
| APU1 Error Code1 |  |  | SUPPLY_ERROR_5V_POS._SW | 59
| APU1 Error Code1 |  |  | AC_SWITCH | 60
| APU1 Error Code1 |  |  | DC_SWITCH | 61
| APU1 Error Code1 |  |  | ENABLE_24V | 62
| APU1 Error Code1 |  |  | DRIVER_VERSION_L1 | 63
| APU1 Error Code1 |  |  | DRIVER_VERSION_L2 | 64
| APU1 Error Code1 |  |  | DRIVER_VERSION_L3 | 65
| APU1 Error Code1 |  |  | CPLD_VERSION | 66
| APU1 Error Code1 |  |  | HW_CONTROL_CARD | 67
| APU1 Error Code1 |  |  | MODEL_CONTROL_CARD | 68
| APU1 Error Code1 |  |  | AC_PRE–CHARGE | 69
| APU1 Error Code1 |  |  | DC_PRE–CHARGE | 70
| APU1 Error Code1 |  |  | SECTOR_SYNCHRONIZATION | 71
| APU1 Error Code1 |  |  | NO_SYNC._SIGNA | 72
| APU1 Error Code1 |  |  | WRONG_FIRMWARE_VERSION | 73
| APU1 Error Code1 |  |  | WRONG_CONTROL_MODE | 74
| APU1 Error Code1 |  |  | WRONG_CONTROL_MODE | 75
| APU1 Error Code1 |  |  | DRIVER_L1 | 76
| APU1 Error Code1 |  |  | DRIVER_L2 | 77
| APU1 Error Code1 |  |  | DRIVER_L3 | 78
| APU1 Error Code1 |  |  | OVER_CURRENT_IDC_HW | 79
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L1_HW | 80
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L2_HW | 81
| APU1 Error Code1 |  |  | OVER_CURRENT_IAC_L3_HW | 82
| APU1 Error Code1 |  |  | PWM_ERROR | 83
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_NEG._HW | 84
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_NEG._HW | 85
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_POS._HW | 86
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VDC_POS._HW | 87
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VDC_TOTAL_HW | 88
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_HW | 89
| APU1 Error Code1 |  |  | OVER_CURRENT_BOOSTER_HW | 90
| APU1 Error Code1 |  |  | DRIVER_CHOPPER | 91
| APU1 Error Code1 |  |  | SUPPLY_ERROR_(3,3V) | 92
| APU1 Error Code1 |  |  | SUPPLY_ERROR_DELAYED_(3,3V) | 93
| APU1 Error Code1 |  |  | DRIVER_BOOSTER | 94
| APU1 Error Code1 |  |  | NO_DRIVER_DETECTED | 95
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL1_LEVEL_4 | 96
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL2_LEVEL_4 | 97
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL3_LEVEL_4 | 98
| APU1 Error Code1 |  |  | OVER_VOLTAGE_MEAN_LEVEL_1 | 99
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_CONTROL_CARD_SW | 100
| APU1 Error Code1 |  |  | WRONG_VERSION_CONTROL_CARD | 101
| APU1 Error Code1 |  |  | VOLTAGE_MEASUREMENT_ISLAND_GRID | 102
| APU1 Error Code1 |  |  | UNBALANCED_GRID_VOLTAGE | 103
| APU1 Error Code1 |  |  | UNBALANCED_PHASE_ANGLE | 104
| APU1 Error Code1 |  |  | UNBALANCED_GRID_CURRENT | 105
| APU1 Error Code1 |  |  | OVER_CURRENT_IDC_SW_POS | 106
| APU1 Error Code1 |  |  | OVER_CURRENT_IDC_SW_NEG | 107
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL1_LEVEL_3 | 108
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL2_LEVEL_3 | 109
| APU1 Error Code1 |  |  | UNDER_VOLTAGE_VL3_LEVEL_3 | 110
| APU1 Error Code1 |  |  | DISCHARGE_UDC_POS | 111
| APU1 Error Code1 |  |  | DISCHARGE_UDC_NEG | 112
| APU1 Error Code1 |  |  | WRONG_OP_MODE_FOR_OVERCURRENT_TEST | 113
| APU1 Error Code1 |  |  | WRONG_VARIANT_TO_UAC_NOM | 114
| APU1 Error Code1 |  |  | SUPPLY_ERROR_24V_POS_MAX_SW | 115
| APU1 Error Code1 |  |  | BLOCKED | 116
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L1_(**) | 117
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L2_(**) | 118
| APU1 Error Code1 |  |  | OVER_TEMPERATURE_IGBT_L3_(**) | 119
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL1_LEVEL_5 | 120
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL2_LEVEL_5 | 121
| APU1 Error Code1 |  |  | OVER_VOLTAGE_VL3_LEVEL_5 | 122
| APU1 Error Code1 |  |  | OVER_VOLTAGE_LEVEL_5_DQ | 123
APU 1 | APU 1 Operating Modes |  |  | ENERGY_SAVING | 0
| APU 1 Operating Modes |  |  | SLEEP | 20
| APU 1 Operating Modes |  |  | OFF | 50
| APU 1 Operating Modes |  |  | DC_CONNECT | 200
| APU 1 Operating Modes |  |  | AC_CONNECT | 500
| APU 1 Operating Modes |  |  | AC_CONNECT_ISLAND_GRID | 600
| APU 1 Operating Modes |  |  | STATCOM_MODE_ACTIVE | 1000
| APU 1 Operating Modes |  |  | CC_CV_MODE_ACTIVE | 2000
| APU 1 Operating Modes |  |  | CC_CV_MODE_ADVANCED | 2001
| APU 1 Operating Modes |  |  | CC_CV+SYNTHETIC_INERTIA_MODE_ACTIVE | 2100
| APU 1 Operating Modes |  |  | CC_CV+SYNTHETIC_INERTIA_MODE_ADVANCED | 2101
| APU 1 Operating Modes |  |  | MPPT_MODE_ACTIVE | 3000
| APU 1 Operating Modes |  |  | ISLAND_GRID_ACTIVE | 4000
| APU 1 Operating Modes |  |  | TEST_BENCH_MODE | 10000
APU 1 | APU 1 Operating Status |  |  | ENERGY_SAVING | 0
| APU 1 Operating Status |  |  | SLEEP | 20
| APU 1 Operating Status |  |  | BOOTING | 30
| APU 1 Operating Status |  |  | OFF | 50
| APU 1 Operating Status |  |  | INIT_DC_CONNECT | 100
| APU 1 Operating Status |  |  | WAIT_DC_CONNECT | 130
| APU 1 Operating Status |  |  | PRECHARGE_DC | 160
| APU 1 Operating Status |  |  | DC_CONNECT | 200
| APU 1 Operating Status |  |  | CONNECTION_CONDITIONS_AC | 300
| APU 1 Operating Status |  |  | INIT_AC_CONNECT | 330
| APU 1 Operating Status |  |  | WAIT_AC_CONNECT | 360
| APU 1 Operating Status |  |  | PRECHARGE_AC | 400
| APU 1 Operating Status |  |  | AC_CONNECT | 500
| APU 1 Operating Status |  |  | AC_CONNECT_ISLAND_GRID | 600
| APU 1 Operating Status |  |  | STATCOM_MODE_ACTIVE | 1000
| APU 1 Operating Status |  |  | STATCOM_CURRENT_LIMIT | 1010
| APU 1 Operating Status |  |  | STATCOM_POWER_LIMIT | 1020
| APU 1 Operating Status |  |  | CC_CV_MODE_ACTIVE | 2000
| APU 1 Operating Status |  |  | POWER_LIMIT_INTERFACE | 2010
| APU 1 Operating Status |  |  | POWER_GRADIENT_STARTUP | 2020
| APU 1 Operating Status |  |  | POWER_LIMIT_P_F | 2030
| APU 1 Operating Status |  |  | CURRENT_LIMIT_AC_FIX | 2110
| APU 1 Operating Status |  |  | CURRENT_LIMIT_AC_DYNAMIC | 2120
| APU 1 Operating Status |  |  | CURRENT_LIMIT_DC_FIX | 2130
| APU 1 Operating Status |  |  | CURRENT_LIMIT_DC_DYNAMIC | 2140
| APU 1 Operating Status |  |  | VOLTAGE_LIMIT_DC | 2150
| APU 1 Operating Status |  |  | MPPT_MODE_ACTIVE | 3000
| APU 1 Operating Status |  |  | MPPT_AC_POWER_LIMIT | 3010
| APU 1 Operating Status |  |  | MPPT_AC_CURRENT_LIMIT | 3020
| APU 1 Operating Status |  |  | MPPT_DC_VOLTAGE_LIMIT | 3030
| APU 1 Operating Status |  |  | MPPT_CONT_TRACKING_UP | 3040
| APU 1 Operating Status |  |  | MPPT_CONT_TRACKING_DOWN | 3050
| APU 1 Operating Status |  |  | MPPT_CYCL_ACTIVE | 3060
| APU 1 Operating Status |  |  | MPPT_WAIT_IDC_MIN | 3070
| APU 1 Operating Status |  |  | MPPT_WAIT_VDC_MIN | 3080
| APU 1 Operating Status |  |  | ISLAND_GRID_START | 4000
| APU 1 Operating Status |  |  | ISLAND_GRID_READY | 4100
| APU 1 Operating Status |  |  | LVRT_SYM | 8100
| APU 1 Operating Status |  |  | LVRT_ASYM_L1 | 8210
| APU 1 Operating Status |  |  | LVRT_ASYM_L2 | 8220
| APU 1 Operating Status |  |  | LVRT_ASYM_L3 | 8230
| APU 1 Operating Status |  |  | LVRT_ASYM2_L12 | 8310
| APU 1 Operating Status |  |  | LVRT_ASYM2_L23 | 8320
| APU 1 Operating Status |  |  | LVRT_ASYM2_L31 | 8330
| APU 1 Operating Status |  |  | HVRT_SYM | 9100
| APU 1 Operating Status |  |  | HVRT_ASYM_L1 | 9210
| APU 1 Operating Status |  |  | HVRT_ASYM_L2 | 9220
| APU 1 Operating Status |  |  | HVRT_ASYM_L3 | 9230
| APU 1 Operating Status |  |  | HVRT_ASYM2_L12 | 9310
| APU 1 Operating Status |  |  | HVRT_ASYM2_L23 | 9320
| APU 1 Operating Status |  |  | HVRT_ASYM2_L31 | 9330
| APU 1 Operating Status |  |  | TEST_BENCH_MODE | 10000